## Contents
Adequacy and Flexibility study 2020-2030 - content of the public consultation
This data is provided in the framework of the Adequacy and Flexibility study covering the years from 2020 to 2030. This study will be published before end of June as requested by law.
It includes data assumptions for Belgium from 2020 to 2030.
Data contained in this document is subject to a public consultation, starting 21/01/2019 and ending 11/02/2019 at 6:00 pm.
Given the longer term horizon of this study (in comparison to the Strategic Reserve Volume evaluation performed each year), the scenario framework is adapted and explained in section 0.
Additional parameters for the flexibility simulations are also being consulted.
Input data for market and flexibility simulations
0. Scenario framework
1. Renewables
2. Nuclear
3. Interconnections
4. Structural block - 'Base case' scenario
4.1 CHP
4.2 Market Response
4.3 Storage
4.4 Needed capacity to ensure SoS and flexibility needs
5. Total electricity consumption
6. Economic and technical variables
6.1. Fuel and CO2 prices
6.2. Investment costs
6.3. Forced outage rates
6.4. Flexibility characteristics
7. Assumptions for other countries

## 0. Scenario framework
0. Scenario framework
The study will determine the volume of adjustable national power, called 'structural block', required to meet the current legal adequacy criteria.
The structural block data consist of the demand side response, storage, CHP and other thermal generation.
The renewables, nuclear and possible import capabilities are not included in the structural block.
For each of the items, the "base case" scenario is being consulted. Additional sensitivities will be also simulated and will depend on the answers received to this consultation.
The "base case" scenario is constructed from the "Energy Pact" ambition from the authorities and was aligned with the FOD Economie - DG Energie, CREG and Plan Bureau.
Scenarios
|  | Type | Base Case | Sensitivity 1 | Sensitivity 2 | …
| Structural block | Market Response | Assumptions
Storage
CHP
|  | CCGT/OCGT | Enough to meet adequacy & flexibility criteria
RES
Nuclear
Imports
Demand
Structural block

## 1. Renewables
1. Evolution of renewable energy sources
Generation capacity at the end of the mentioned year [MW]
Generation type |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Renewable production |  | 6860 | 7588 | 8473.7238 | 9802.4252 | 11378.4113 | 12080.1231 | 12486.8563 | 12893.5895 | 13300.3227 | 13707.0559 | 14113.7891 | 14520.5223 | 16927.2555 | 17333.9887 | 17740.7219
| Wind | 2371 | 2774 | 3305 | 4123 | 5046 | 5210 | 5350 | 5490 | 5631 | 5771 | 5911 | 6051 | 8191 | 8331 | 8471
| Wind onshore | 1658 | 1915 | 2254 | 2513 | 2775 | 2939 | 3079 | 3219 | 3360 | 3500 | 3640 | 3780 | 3920 | 4060 | 4200
| Wind offshore | 713 | 859 | 1051 | 1610 | 2271 | 2271 | 2271 | 2271 | 2271 | 2271 | 2271 | 2271 | 4271 | 4271 | 4271
| Photovoltaics | 3200 | 3587 | 3931.7835 | 4432.8081 | 5069.8328 | 5600.129 | 5866.7813 | 6133.4337 | 6400.086 | 6666.7383 | 6933.3907 | 7200.043 | 7466.6953 | 7733.3477 | 8000
| Biofuel | 844 | 794 | 803.575 | 814.6796 | 826.069 | 830.0552 | 830.0552 | 830.0552 | 830.0552 | 830.0552 | 830.0552 | 830.0552 | 830.0552 | 830.0552 | 830.0552
| Biomass - individually modelled | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348
| Biomass - profiled | 496 | 446 | 455.575 | 466.6796 | 478.069 | 482.0552 | 482.0552 | 482.0552 | 482.0552 | 482.0552 | 482.0552 | 482.0552 | 482.0552 | 482.0552 | 482.0552
| Waste | 331 | 319 | 319 | 314 | 314 | 314 | 314 | 314 | 314 | 314 | 314 | 314 | 314 | 314 | 314
| Waste - individually modelled | 280 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268
| Waste - profiled | 51 | 51 | 51 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
| Hydro RoR | 114 | 114 | 114 | 118 | 123 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126

## 2. Nuclear
2. Evolution of nuclear generation
Generation capacity at the end of the mentioned year [MW]
Generation type | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Nuclear | 5919 | 5919 | 5919 | 5919 | 5919 | 5919 | 4913 | 3905 | 3905 | 0 | 0 | 0 | 0 | 0 | 0
The reference assumption on the existing nuclear generation in Belgium is exclusively based on the current law. The planned decommissioning dates for each nuclear reactor are:
- Doel 3: 1st October 2022;
- Tihange 2: 1st February 2023;
- Doel 1: 15 February 2025;
- Doel 4: 1st July 2025;
- Tihange 3: 1st September 2025;
- Tihange 1: 1st October 2025;
- Doel 2: 1st December 2025.
Source :
www.ejustice.just.fgov.be/cgi_loi/loi_a.pl?language=fr&caller=list&cn=2003013138&la=f&fromtab=loi&sql=dt=%27loi%27&tri=dd+as+rank&rech=1&numero=1

## 3. Interconnections
3. Interconnections
Elia aims to model the cross-border exchanges with a "flow based" methodology which will beter represent what is currently used in the CWE day-ahead market coupling (instead of the "NTC methodology" used in medium and long term studies).
Such "flow based" approach is already applied for shorter term adequacy studies (until Y+3). It is important to note that given the further horizons studied in this study (until Y+10), applying the same methodology is not representative (changes in the grid, generation location, market design).
Elia is therefore working on setting up a simplified "flow based method" to be used for this study. The method and data being not ready at the moment of this public consultation, they cannot be consulted.
As input for the grid investments, Elia will take into account the following key documents:
- Elia Federal Development Plan: | http://www.eliafederaldevelopmentplan.be/
- Ten year Network Development Plan: | https://tyndp.entsoe.eu/
For an idea of given capacities to the market, the market parties can reffer to the "flow based domains" consulted in the framework of:
- the Strategic Reserve Volume evaluation: | http://www.elia.be/~/media/files/Elia/Products-and-services/Strategic-Reserve/2018/20181128_Adequacy-study.pdf
Or the NTC values used in:
- the previous adequacy and flexibility study performed by Elia in 2016: | http://www.elia.be/en/about-elia/newsroom/news/2016/20-04-2016-Adequacy-study-flexibility-Belgian-electricity-system
Default NTC set used in the framework of long term studies at ENTSO-E and Elia from 2025 onwards
Borders | NTC 2025 [MW] (from-to/to-from)
BE-FR | 2800/4300
BE-NL | 3400/3400
BE-GB | 1000/1000
BE-DE | 1000/1000
BE-LU | 300/180
NTC data for other countries are available in the ENTSO-E plateform : | https://www.entsoe.eu/Documents/SDC%20documents/MAF/MAF_2018_Dataset.xlsx

## 4.1. CHP
4.1. Cogeneration generation summary
Generation capacity at the end of the mentioned year[MW]
Generation type |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Gas CHP |  | 1990 | 1837.4 | 1890.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4 | 1970.4
| Individually modelled | 776 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4 | 726.4
| Profiled | 1214 | 1111 | 1164 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244

## 4.2. Market Response
4.2. Market Response
Market response volumes can be considered as distributed capacity that can be activated when prices are above a certain level and for a limited time duration (depending on several constraints). These include shedding and shifting of consumption, storage and even small scale generators (not taken into account as generation units in the model such as for instance emergency generators). For this study, as the goal is to assess if the system can cope with the adequacy and total flexibility requirements, no distinction is made between flexibility provided through the TSO (i.e. as ancillary services) and flexibility provided through the market. The market response volumes will include the total available market response in Belgium (including those participating today as ancillary services). This is contrast to the yearly adequacy study for the determination of the strategic reserve where the market response volume excludes the volume for ancillary services, modelled explicitly as balancing capacity.
Market response volume per year (including the ones participating to the ancillary services)
Voulme at the end of the mentioned year[MW]
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Total volume | 1236 | 1316 | 1403 | 1496 | 1513 | 1532 | 1547 | 1565 | 1765 | 1965 | 2165 | 2365 | 2565
Max use of 1 hour | 79 | 82 | 87 | 93 | 95 | 97 | 98 | 100 | 120 | 140 | 160 | 180 | 200
Max use of 2 hours | 275 | 287 | 304 | 326 | 332 | 338 | 344 | 350 | 420 | 490 | 560 | 630 | 700
Max use of 4 hours | 528 | 578 | 622 | 658 | 660 | 662 | 663 | 665 | 685 | 705 | 725 | 745 | 765
Max use of 8 hours | 236 | 246 | 260 | 279 | 284 | 290 | 295 | 300 | 360 | 420 | 480 | 540 | 600
No limit | 118 | 123 | 130 | 140 | 142 | 145 | 147 | 150 | 180 | 210 | 240 | 270 | 300
Voulme at the end of the mentioned year [GWh/day in winter period]
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Total demand shifting volume [GWh/day in winter period] | 0 | 0 | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.9 | 1.1 | 1.3 | 1.5

## 4.3. Storage
4.3 Storage
| BE storage facilities |  | Production capacity at the end of the mentioned year [MW]
|  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Pumped storage
| Capacity [MW] | Pumped-storage | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308 | 1308
| Reservoir volume [MWh] | Storage reservoir | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
|  | Available storage for economical dispatch | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
Other storage facilities
| Total capacity [MW] |  | 0 | 7 | 25.5 | 94.7143 | 100 | 280 | 460 | 640 | 820 | 1000 | 1120 | 1240 | 1360 | 1480 | 1600
|  | Large scale storage | 0 | 7 | 25.5 | 94.7143 | 163.9286 | 233.1429 | 302.3571 | 371.5714 | 440.7857 | 510 | 530.5 | 551 | 571.5 | 592 | 612.5
| Capacity [MW] | Small scale storage | 0 | 0 | 0 | 0 | 0 | 68 | 136 | 204 | 272 | 340 | 394.5 | 449 | 503.5 | 558 | 612.5
|  | Vehicule-to-grid | 0 | 0 | 0 | 0 | 0 | 30 | 60 | 90 | 120 | 150 | 195 | 240 | 285 | 330 | 375
|  | Large scale storage | 0 | 7 | 25.5 | 94.7143 | 163.9286 | 233.1429 | 302.3571 | 371.5714 | 440.7857 | 510 | 530.5 | 551 | 571.5 | 592 | 612.5
| Reservoir volume [MWh] | Small scale storage | 0 | 0 | 0 | 0 | 0 | 204 | 408 | 612 | 816 | 1020 | 1183.5 | 1347 | 1510.5 | 1674 | 1837.5
|  | Vehicule-to-grid | 0 | 0 | 0 | 0 | 0 | 120 | 240 | 360 | 480 | 600 | 780 | 960 | 1140 | 1320 | 1500

## 4.4. Additional to Sos-Flex
4.4. Additional capacity to meet adequacy and flexibility requirements
For each scenario and timehorizon, a certain need for additional capacity might be identified.
That need will already take into account all the generation, storage, interconnections and demand response listed in this document.
The needed capacity will then be filled with thermal generation in the form of CCGT or OCGT.
It is important to note that other forms of capacity are already taken into account in the scenario definition and sensitivities will be performed to those.

## 5. Tot. electricity consumption
5. Total electricity consumption
IHS Markit
|  | Historical values |  |  | Base case normalized total demand
|  | Total demand [TWh] | Normalised total demand [TWh] | Growth rate | Growth rate | Forecast [TWh]
historical | 2011 | 87.02 | 88.1684 | -0.012311
historical | 2012 | 84.857 | 84.6645 | -3.974%
historical | 2013 | 86.239 | 85.8137 | 1.357%
historical | 2014 | 83.728 | 85.1404 | -0.7846%
historical | 2015 | 85.009 | 85.6376 | 0.584%
historical | 2016 | 85.02 | 84.86 | -0.908%
historical | 2017 | 84.826 | 85.38 | 0.6128% |  | 85.38
forecast | 2018 |  |  |  | 0.589% | 85.8829
forecast | 2019 |  |  |  | 0.6574% | 86.4475
forecast | 2020 |  |  |  | 0.7364% | 87.0841
forecast | 2021 |  |  |  | 0.6192% | 87.6234
forecast | 2022 |  |  |  | 0.4894% | 88.0522
forecast | 2023 |  |  |  | 0.5041% | 88.4961
forecast | 2024 |  |  |  | 0.5139% | 88.9509
forecast | 2025 |  |  |  | 0.5595% | 89.4486
forecast | 2026 |  |  |  | 0.6045% | 89.9893
forecast | 2027 |  |  |  | 0.6341% | 90.56
forecast | 2028 |  |  |  | 0.6377% | 91.1374
forecast | 2029 |  |  |  | 0.6068% | 91.6905
forecast | 2030 |  |  |  | 0.5471% | 92.1921
Source : | European Planning Scenario from IHS Markit - July 2018

## 6.1. Fuel and CO2 prices
6.1. Fuel and CO2 prices
Fuel and CO2 prices per year
Source : IEA - World Energy Outlook 2018 (New Policies scenario)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Gas TTF [€/MWh] | 20.2 | 20.98 | 21.76 | 22.54 | 23.32 | 24.1 | 24.32 | 24.54 | 24.76 | 24.98 | 25.2
Coal ARA [$/mt] | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CO2 EUA [€/tCO2] | 19.7 | 20.26 | 20.82 | 21.38 | 21.94 | 22.5 | 23.6 | 24.7 | 25.8 | 26.9 | 28

## 6.2. Investment costs
6.2. Economic assumptions
Type of units | CAPEX (€/kW) |  | Economic Lifetime (yr) | FOM (€/kW) | Source
| 2016 | 2030
New CCGT | 850 | 850 | 20 | 21 | https://setis.ec.europa.eu/system/files/ETRI_2014.pdf
New OCGT | 550 | 550 | 20 | 17 | https://setis.ec.europa.eu/system/files/ETRI_2014.pdf
New CHP | 880 | 880 | 20 | 75 | https://setis.ec.europa.eu/system/files/ETRI_2014.pdf
Storage Coo 3 | - | 1000 | 25 | 45 | http://corporate.engie-electrabel.be/fr/actualite/coo-une-solution-de-stockage-a-grande-echelle-et-flexible/
Coo 1,2 & Plate Taille | - | - | - | 45 | https://setis.ec.europa.eu/system/files/ETRI_2014.pdf
Large-scale batteries (assuming 1 hour energy limit) | 600 | 253 | 10 | 15 | https://ec.europa.eu/energy/sites/ener/files/documents/2018_06_27_technology_pathways_-_finalreportmain2.pdf
Small-scale batteries (assuming 3 hours energy limit) | 810 | 342 | 10 | 6 | https://ec.europa.eu/energy/sites/ener/files/documents/2018_06_27_technology_pathways_-_finalreportmain2.pdf
DSM shedding (industrial) | 0 | 0 | - | 10 | https://www.cre.fr/documents/deliberations/proposition/effacements-de-consommation/annexe-4-etude-des-avantages-que-l-effacement-procure-a-la-collectivite-et-de-leur-integration-dans-un-dispositif-de-prime
DSM shifting residential | 450€/device | 450€/device | 8 | 10 | https://www.cre.fr/documents/deliberations/proposition/effacements-de-consommation/annexe-4-etude-des-avantages-que-l-effacement-procure-a-la-collectivite-et-de-leur-integration-dans-un-dispositif-de-prime

## 6.3. FO rates
6.3. Forced outage rates
| Average forced outage rate over 2007-2017 [%] | Average duration of forced outage rate (2007-2017) [days] | Number of FO per year
Nuclear | 3.45% | 7 | 1
Classical | 7.94% | 3 | 6
CCGT | 8.86% | 4 | 5
GT | 12.3% | 6 | 3
TJ | 4.3% | 4 | 2
Waste | 1.5% | 3 | 1
CHP | 6.4% | 5 | 4
Pumped storage | 4.3% | 6 | 2
DC links | 5% | 7 | 2

## 6.4. Flex. charact.
6.4. Flexibility characteristics
| Parameters | [8 empty] | Maximum upward flexibility |  |  | Maximim downward flexibility |  |  | Energy Limit | Clarification, justifications and remarks
Parameter | Minimum up time | Minimum down time | Hot start up time | Warm start up time | Cold start up time | Transition time from "hot" to "warm" | Transition time from "warm" to "cold" | Min Stable power | Ramp Rate | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit
Definition | Duration that a unit needs to remain in "on" status after the start of an activation | Duration that a unit needs to remain in "off" status after the end of an activation | Duration between the activation signal and attaining minimum stable power in "hot", "warm" or "cold" conditions |  |  | Duration that a unit goes from "hot" to "warm" status after the end of an activation | Duration that a unit goes from "warm" to "cold" status after the end of an activation | Minimum power output level when in "on" status | Minimum power variation in a time period | Maximum share of the installed capacity which can participate in the categories upward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | Maximum share of the installed capacity which can participate in the categories downward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | expressed in number of hours during which the plant can product at its maximum capacity
Unit | hours | hours | hours | hours | hours | hours | hours | % Pmax | %Pmax/min | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | hours
Nuclear
Interconnections (AC & DC) | [10 empty] | 50 MW | min(ATC import -Pnom import) |  | 350 MW | min(ATCexport - Pnom export) |  | Fast flexibility is constrained by current sharing capacity which is considered as firm [1]; Slow flexibility constrained by remaining import / export capacity after day-ahead
Renewable Generation
Wind offshore | [8 empty] | 100% |  |  |  | 65% Pnom | 65% Pnom | 65% Pom |  | Based on literature [2] and further constrained based on an analysis of day-ahead forecast errors
Wind onshore (only share CIPU) | [8 empty] | 100% |  |  |  | 88% Pnom | 88% Pnom | 88% Pnom |  | Based on literature [2] and further constrained based on an analysis of day-ahead forecast errors
Photovoltaics
Run-of-River Hydro
Biofuel (only share CIPU) | 8h | 8h | 3h | 5h | 7h | 12h | 72h | 40% | 3% |  |  |  | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and CHP recent steam turbine values
CCGT
new (to be commissioned) | 2h | 2h | 0.5h | 1.5h | 2h | 8h | 48h | 30% | 11% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [4] and [5]
recent (commissioned after 2000) | 3h | 3h | 1h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
old (commissioned before 2000) | 3h | 3h | 1.5h | 2,5h | 4h | 8h | 48h | 45% | 3% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
OCGT
new | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 20% | 15% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [4] and [5]
existing | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 30% | 12% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
CHP (only share CIPU) | 8h | 8h | 3h | 5h | 7h | 12h | 72h | 40% | 3% |  |  |  | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | 8 hours | Based on literature [4] and CHP recent steam turbine values (+ [6] for energy limit)
Pumped Storage | [8 empty] | 100% | Pmax- Pnom (0% when "off") | Pmax - Pnom | Pmax - Pnom | Pnom- Pmax- (0% when "off") | Pnom - Pmax- | Pnom - Pmax- | 4,5 hours | Aggregation of PHS-sites. Based on literature review [7; 8] and Elia's internal information
Demand Response
CAT-1h | [8 empty] | 100% |  |  | Pmax - Pnom |  |  |  | 1 | Based in E-CUBE study [9] and Elia's best estimate. Share of 86% evolves towards 74% from 2020 to 2030.
CAT-2h | [8 empty] | 100% |  |  | Pmax - Pnom |  |  |  | 2
CAT-4h | [8 empty] | 100% |  | min (85% Pmax ; Pmax - Pnom) | Pmax - Pnom |  |  |  | 4
CAT-8h | [8 empty] | 100% |  |  | Pmax- Pnom |  |  |  | 8
CAT-nolimit | [8 empty] | 100% |  |  | Pmax - Pnom
New technologies
Small scale storage | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmax- | Pnom - Pmax- | Pnom - Pmax- | 3 hours | Based on literature review [10;11;12], Elia's best estimate
Large scale storage | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmax- | Pnom - Pmax- | Pnom - Pmax- | 1 hours
Consumption shifting | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom
Vehicle to Grid (V2G) | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmax- | Pnom - Pmax- | Pnom - Pmax- | 3 hours
Terminology
Pmax | Maximum injected power of the unit (MW)
Pmax- | Maximum absorbed power of the unit (MW), i.e. negative value
Pnom | Day-Ahead Scheduled power of the unit (MW), i.e. positive or negative value
Pmin | Minimum stable power (MW)
ATCexport | Maximum available export capacity (MW)
ATCimport | Maximum available import capacity (MW)
ramping flex | Capacity which can be regulated continuously up- or downward in a timeframe of one minute (expressed as MW/min)
fast flex | Capacity which can be regulated up- or downward in a time frame of 15 minutes
slow flew | Capacity which can be regulated up- or downward in a time frame of 5 hours
List of references
1 | CREG | Décision sur la demande d’approbation de la méthode d’évaluation et de la détermination de la puissance de réserve primaire, secondaire et tertiaire pour 2019 | [9 empty] | https://www.creg.be/fr/publications/decision-b1808
2 | Vestas | Wind Energy and Ancillary Services | [9 empty] | http://www.anev.org/wp-content/uploads/2018/02/180216-Wind-Energy-Ancillary-Services-ANEV-Italy_Vestas.pdf
3 | Dotzauer et al. | How to measure flexibility – Performance indicators for demand driven power generation from biogas plants | [9 empty] | https://www.sciencedirect.com/science/article/pii/S0960148118312059#sec3
4 | ENTSO-E | MAF Data | [9 empty] | https://www.entsoe.eu/Documents/SDC%20documents/MAF/MAF_2018_Dataset.xlsx
5 | Agora | Flexibility in thermal power plants, with a focus on existing coal-fired power plants | [9 empty] | https://www.agora-energiewende.de/fileadmin2/Projekte/2017/Flexibility_in_thermal_plants/115_flexibility-report-WEB.pdf
6 | Danish Energy Agency | Flexibility in the Power System - Danish and European experiences | [9 empty] | https://ens.dk/sites/ens.dk/files/Globalcooperation/flexibility_in_the_power_system_v23-lri.pdf
7 | Deloitte | Assessing the economic conditions of Belgian pumped-hydroelectric storage: comparative review of profitability drivers in Europe and evaluation of the current situation | [9 empty] | https://www.creg.be/sites/default/files/assets/Consult/2018/1718/RA1718-Annex2.7.pdf
8 | e-Storage | Potential, Economic and Environmental Value of Large-Scale Energy Storage in Europe | [9 empty] | http://www.estorage-project.eu/wp-content/uploads/2013/06/eStorage-D3.2-Value-of-storage.pdf
9 | E-Cube Strategy Consultants | Market Response study 2017 – 2nd phase report | [9 empty] | https://www.elia.be/~/media/files/Elia/Products-and-services/Strategic-Reserve/Elia_Market%20Response_Implementation%20report.pdf
11 | Gils, H. | Assessment of the theoretical demand response potential in Europe | [9 empty] | https://ac.els-cdn.com/S0360544214001534/1-s2.0-S0360544214001534-main.pdf?_tid=d4fce1a0-6f34-465d-9c4f-523e95750e30&acdnat=1546943860_20cd8cd6d9355dd840de7e4fd94255bb
11 | Le Baut et al. | Characterization of flexibility resources and distribution networks | [9 empty] | http://smartnet-project.eu/wp-content/uploads/2017/05/D1.2_20170522_V1.1.pdf
12 | Brouwer et al. | Least-cost options for integrating intermittent renewables in low-carbon power systems | [9 empty] | https://ac.els-cdn.com/S0306261915012167/1-s2.0-S0306261915012167-main.pdf?_tid=52eeb980-f5b2-43f0-8d14-83cd9f435f58&acdnat=1546889876_5b2bf335e121403ca7dc9296eaf88b19

## 7. Sources for other countries
6. Sources for other countries
The most up-to-date information will be used for other countries. The list below gives the main sources that will be used. On top of it, Elia will confirm the data with the respective TSOs and take any relevant information from the market into account.
Country | Source - more information
The Netherlands
'Monitoring report' from Tennet | http://files.smart.pr/70/33fbb0037611e9974b07bf97787b0f/20181218-Rapport-Monitoring-Leveringszekerheid-2018-_2017-2033_.pdf
France
Bilan prévisionnel RTE | https://www.rte-france.com/fr/article/bilan-previsionnel
Germany
TSOs Grid Reserve analysis | https://www.bundesnetzagentur.de/DE/Sachgebiete/ElektrizitaetundGas/Unternehmen_Institutionen/Versorgungssicherheit/Netzreserve/netzreserve-node.html
Great-Britain
'Future Energy Scenario' 2018 - Steady Progression | http://fes.nationalgrid.com/
Other countries
Mid-Adequacy Forecast 2019 from ENTSO-E | https://www.entsoe.eu/outlooks/midterm/
Ten Year Network Development Plan - ENTSO-E | https://tyndp.entsoe.eu/
Pentalateral Energy Forum adequacy asessment | www.benelux.int/nl/kernthemas/holder/energie/pentalateral-energy-forum