## Contents
CRM - Public consultation
Delivery Year 2026 - Inputs for Y-4 Auction
This data is provided in the framework of the evaluation of the Belgian CRM calibration.
It includes the data required by article 5, §2 of the FPS' Royal Decree proposal
All the data presented in this excel are targetting the time horizon 2026-27 that will be simulated for the calibration.
1° Data and assumptions for the scenario
1. Generation & Storage
1.1 Generation & Storage summary
1.2 Individually modelled thermal generation
1.3 Storage
1.4 Renewable and non-CIPU
1.5 Forced outage rates
2. Consumption
2.1 Demand
2.2 Demand-Side Response
3. Balancing capacity
4. Flow based domains
5. Other countries data
6. Economic parameters
2° Sensitivities that could be integrated in the reference scenario
7 Sensitivities menu
3° Preselected capacity types
8. Preselected capacity types
4° Scenarios post-delivery period
9. Scenarios post delivery year
5° Intermediate Price Cap
10. Parameters for the IPC
10.1 Technology list
10.2 Activation cost avail. test
10.3 Net revenues balancing

## 1.1 Summary
1.1 Generation & Storage summary
Generation type |  |  | Generation capacity [MW] | Comment
Individually modelled non renewable thermal generation |  |  | 5585.9
NU | Nuclear |  | 0
CCGT | Gas |  | 3820.5
OCGT | Gas |  | 599
CHP | Gas |  | 1008.4
| Oil |  | 158 | Assuming all existing TJ remain
Profiled thermal non renewable generation |  |  | 1379 | Adequacy and flexibility (2021) and Strategic Reserve (2020)
Renewable generation |  |  | 16575.4
| Wind |  | 6931
|  | Onshore | 3978 | Based on final NECP (WAM scenario)
|  | Offshore | 2953 | Based on final NECP (WAM scenario)
| Photovoltaics |  | 8600 | Based on final NECP (WAM scenario)
| Hydro RoR |  | 140 | Based on final NECP (WAM scenario)
| Biomass |  | 572
|  | individually modelled | 68
|  | profiled | 504 | Adequacy and flexibility (2021) based on NECP
| Waste |  | 332.4
|  | individually modelled | 286.4
|  | profiled | 46 | Adequacy and flexibility (2021) based on NECP
Storage |  |  | 1981
| Pumped storage |  | 1224
| Batteries |  | 757 | Adequacy and flexibility (2021)

## 1.2 Ind. mod. thermal gen.
1.2 Individually modelled thermal generation
This list contains all the individually modelled thermal generation, their type and their generation capacity. This section is presented in §2.1.1.2. of the explanatory note.
Owner | Generation unit name | Type | Fuel type | Derating type | Generation capacity [MW] | Comment
Engie - Electrabel | AALST SYRAL GT | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | AALST SYRAL ST | CHP | Gas | CHP, waste & biomass | 5
Engie - Electrabel | AALTER TJ | TJ | Oil | TJ | 18
Engie - Electrabel | AMERCOEUR 1 GT | CCGT-GT | Gas | CCGT | 289
Engie - Electrabel | AMERCOEUR 1 ST | CCGT-ST | Gas | CCGT | 162
Luminus | ANGLEUR TG 31 | GT | Gas | OCGT | 25
Luminus | ANGLEUR TG 32 | GT | Gas | OCGT | 25
Luminus | ANGLEUR TG 41 | GT | Gas | OCGT | 64
Luminus | ANGLEUR TG 42 | GT | Gas | OCGT | 64
Engie - Electrabel | AWIRS 4 | CL | Biomass | CHP, waste & biomass | - | Considered out of the market in MAF 2020
Engie - Electrabel | BEERSE TJ | TJ | Oil | TJ | 32
Indaver | Beveren 2 Indaver | IS | Waste | CHP, waste & biomass | 21
Indaver | Beveren 3 Indaver | IS | Waste | CHP, waste & biomass | 24
Engie - Electrabel | Beveren Ineos Phenol Chem | CHP | Gas | CHP, waste & biomass | 25.1
Indaver | Beveren Sleco | IS | Waste | CHP, waste & biomass | 41
Biopower | BIOMASSA OOSTENDE | IS | Biomass | CHP, waste & biomass | 18
Biostoom | BIOSTOOM OOSTENDE | IS | Waste | CHP, waste & biomass | 19.4
Borealis | Borealis Kallo Cogen GT_ST | CHP | Gas | CHP, waste & biomass | 32
Engie - Electrabel | CIERREUX TJ | TJ | Oil | TJ | 18
Engie - Electrabel | DOEL 2 | NU | Nuclear | NU | - | Decommissioned on 1st December 2025
Engie - Electrabel | DROGENBOS GT1 | CCGT-GT | Gas | CCGT | 150
Engie - Electrabel | DROGENBOS GT2 | CCGT-GT | Gas | CCGT | 150
Engie - Electrabel | DROGENBOS ST | CCGT-ST | Gas | CCGT | 160
Euro-silo | Euro-Silo | CHP | Gas | CHP, waste & biomass | 12.9
Indaver | E-wood | IS | Waste | CHP, waste & biomass | 22
Engie - Electrabel | Fluxys Zeebrugge | CHP | Gas | CHP, waste & biomass | 40
Green Power | Greenpower Oostende | IS | Waste | CHP, waste & biomass | 20
Luminus | HAM 31 | GT | Gas | OCGT | 58
Luminus | HAM 32 | GT | Gas | OCGT | 58
Luminus | HAM Gent-GT | CHP | Gas | CHP, waste & biomass | 39
Luminus | HAM Gent-ST | CHP | Gas | CHP, waste & biomass | -
Engie - Electrabel | HERDERSBRUG GT1 | CCGT-GT | Gas | CCGT | 157
Engie - Electrabel | HERDERSBRUG GT2 | CCGT-GT | Gas | CCGT | 156.3
Engie - Electrabel | HERDERSBRUG ST | CCGT-ST | Gas | CCGT | 167
INEOS | INESCO GT1 | CHP | Gas | CHP, waste & biomass | 44.8
INEOS | INESCO GT2 | CHP | Gas | CHP, waste & biomass | 44.8
INEOS | INESCO ST | CHP | Gas | CHP, waste & biomass | 48.5
INTRADEL | INTRADEL | IS | Waste | CHP, waste & biomass | 32
IPALLE | Ipalle THUMAIDE | IS | Waste | CHP, waste & biomass | 34
Engie - Electrabel | ISVAG | IS | Waste | CHP, waste & biomass | 12
Lampiris | IVBO | IS | Waste | CHP, waste & biomass | 16
Engie - Electrabel | IXELLES-VOLTA TJ | TJ | Oil | TJ | 18
Luminus | IZEGEM | CHP | Gas | CHP, waste & biomass | 20
Inovyn | JEMEPPE-SUR-SAMBRE GT1 | CHP | Gas | CHP, waste & biomass | 48
Inovyn | JEMEPPE-SUR-SAMBRE GT2 | CHP | Gas | CHP, waste & biomass | 48
Inovyn | JEMEPPE-SUR-SAMBRE ST | CHP | Gas | CHP, waste & biomass | 10
Engie - Electrabel | KNIPPEGROEN STEG | GT | Gas | OCGT | 305
Lillo Energy | Lillo Degussa GT1 | CHP | Gas | CHP, waste & biomass | 43
Lillo Energy | Lillo Degussa GT2 | CHP | Gas | CHP, waste & biomass | 32
Lillo Energy | Lillo Degussa ST | CHP | Gas | CHP, waste & biomass | 10
Direct Energie | MARCINELLE ENERGIE TGV | CCGT | Gas | CCGT | 413
Engie - Electrabel | MONSANTO LILLO WKK EBL | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | NOORDSCHOTE TJ | TJ | Oil | TJ | 18
Engie - Electrabel | Oorderen Bayer | CHP | Gas | CHP, waste & biomass | 43
Luminus | RINGVAART STEG | CCGT | Gas | CCGT | 385
Engie - Electrabel | RODENHUIZE 4 | CL | Biomass | CHP, waste & biomass |  | Considered out of the market as of 2023
Engie - Electrabel | SAINT-GHISLAIN STEG | CCGT | Gas | CCGT | 350
Engie - Electrabel | SAPPI LANAKEN GT | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | Schaerbeek SIOMAB 1 | IS | Waste | CHP, waste & biomass | 15
Engie - Electrabel | Schaerbeek SIOMAB 2 | IS | Waste | CHP, waste & biomass | 15
Engie - Electrabel | Schaerbeek SIOMAB 3 | IS | Waste | CHP, waste & biomass | 15
EXXONMOBIL | SCHELDELAAN EXXONMOBIL | CHP | Gas | CHP, waste & biomass | 140
Luminus | SERAING TG1 | CCGT-GT | Gas | CCGT | 150
Luminus | SERAING TG2 | CCGT-GT | Gas | CCGT | 150
Luminus | SERAING TGV | CCGT-ST | Gas | CCGT | 170
STORA | STORA LANGERBRUGGE CHP 1 | CHP | Biomass | CHP, waste & biomass | 10
STORA | STORA LANGERBRUGGE CHP 2 | CHP | Biomass | CHP, waste & biomass | 40
Taminco | TAMINCO GENT CHP | CHP | Gas | CHP, waste & biomass | 6.3
T-Power | T-POWER | CCGT | Gas | CCGT | 425
Engie - Electrabel | VILVOORDE GT | CCGT-GT | Gas | CCGT | -
TOTAL | WILMARSDONK TOTAL GT1 | CHP | Gas | CHP, waste & biomass | 43
TOTAL | WILMARSDONK TOTAL GT2 | CHP | Gas | CHP, waste & biomass | 43
TOTAL | WILMARSDONK TOTAL GT3 | CHP | Gas | CHP, waste & biomass | 43
Zandvliet Power NV | ZANDVLIET POWER | CCGT | Gas | CCGT | 386.2
Engie - Electrabel | ZEDELGEM TJ | TJ | Oil | TJ | 18
Engie - Electrabel | ZEEBRUGGE TJ | TJ | Oil | TJ | 18
Engie - Electrabel | ZELZATE TJ | TJ | Oil | TJ | 18
Engie - Electrabel | Zwijndrecht Lanxess GT | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | Zwijndrecht Lanxess ST | CHP | Gas | CHP, waste & biomass | 15
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit

## 1.3 Storage
1.3 Storage
This section is presented in §2.1.1.3. of the explanatory note.
1.3.1 Pumped-Storage
| BE Pumped-Storage facilities |  | Reservoir Volume [MWh]
| Storage reservoir |  | 5800
| Storage reservoir derating (ancillary services) |  | 500
| Available storage for economical dispatch |  | 5300
| Unit name |  | Turbining capacity [MW]
| Total capacity |  | 1224
| Coo 1-6 |  | 1080
| Platte Taille 1-4 |  | 144
1.3.2 Batteries
a) Definition in the ERAA methodology regarding batteries:
In-the-market batteries, which are large-scale battery capacities that are traded in day-ahead and intraday markets. In-the-market batteries shall be modelled similarly to pumped-hydro storage and shall be subject to the following constraints: maximum power, maximum energy storage, state of charge, charging/discharging efficiency; Out-of-market batteries, which represent small-scale batteries typically managed behind the meter. Out-of-market batteries shall be modelled as peak-shaving units based on predefined peak-reduction ratios, which are a direct input to the demand prediction process
Three categories are considered for "batteries" in this study: large scale batteries, small scale batteries and Vehicle-to-Grid (V2G).
The small scale batteries are assumed to be managed behind the meter and are considered for this reason in the "out-of-market" category.
The large scale batteries are assumed to participate to the electricity market and are considered for this reason in "in-the-market" category.
The capacity for V2G is shared between "in-the-market" and "out-of-market" categories as a part was assumed reacting to market prices and another to local behind the meter optimization. This share evolves with time as described in the table below.
| Total capacity [MW] |  | 756.7
| Capacity [MW] | Large scale storage ("in-the-market") | 411.8
|  | Small scale storage ("out-of-market") | 215.5
|  | Vehicule-to-Grid (V2G) | 129.4
|  | V2G "in-the-market" | 18.1
|  | V2G "out-of-market" | 111.2
| Reservoir volume [MWh] | Large scale storage ("in-the-market") | 824
| Reservoir volume [MWh] | Small scale storage ("out-of-market") | 646.6
|  | Vehicule-to-grid | 517.4
|  | V2G "in-the-market" | 72.4
|  | V2G "out-of-market" | 445

## 1.4 Renewable and non-CIPU
1.4 Renewable energy sources and non-CIPU thermal units
This section is presented in §2.1.1.4. of the explanatory note.
Generation type |  | Generation capacity [MW]
| Wind | 6851
| Wind onshore | 3978
| Wind offshore | 2953
| Photovoltaics | 8600
| Hydro RoR | 140
| Gas CHP - non-CIPU | 1379
| Biomass - non-CIPU | 504
| Waste - non-CIPU | 46

## 1.5 Forced outage rates
1.5 Forced outage rates
This section is presented in §2.1.1.5. of the explanatory note.
Average forced outage rate over 2011-2020
CCGT | 8.379%
GT | 9.223%
TJ | 3.577%
CHP, waste & biomass | 7.005%
Pumped storage | 4.512%
HVDC link | 6%
Sources:
Elia (2011-2020)
ENTSO-E Transparency platform (2015-2020) where available
MAF Study

## 2.1 Demand
2.1 Demand
§2.1.2.1. of the explanatory note describes this section.
|  | Total demand [TWh] | Normalised total demand [TWh]
historical | 2019 | 84.89 | 85.68
| 2020 | 81 | 82
Total demand forecasted | 2026 |  | 90.2
Sources:
The total electricity demand for Belgium is based on the tool developped by Climact in the scope of the strategic reserve study where the methodology used is described in the following report:
https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2020/20200603_total-electricity-demand-forecasting_en.pdf
The macro-economic input data used in the tool are based on the report published by Federal Plan Bureau on June 2020:
https://www.plan.be/publications/publication-2009-fr-perspectives_economiques_2020_2025_version_de_juin_2020
The assumptions for electrification are based on the final National Energy and Climact Plan following the two scenarios proposed by the regional and federal authorities : 'With Additional Measures" (WAM) and "With Expected Measures" (WEM), more info on the following website:
https://climat.be/politique-climatique/belge/nationale/plan-national-energie-climat-2021-2030

## 2.2 Demand-Side Response
2.2 Demand-Side Response
This section is presented in §2.1.2.2. of the explanatory note.
a) Definition in the ERAA methodology regarding Demand-Side Response (DSR):
'explicit demand-side response’ (explicit DSR) means the change of electric demand pursuant to an accepted offer to sell demand reduction or increase in an organised market, either directly or through aggregation. Explicit DSR may consist of either foregone or time-shifted demand;
‘implicit demand-side response’ (implicit DSR) means the change of demand by final customers from their normal or current consumption patterns, in response to time-variable electricity prices or incentive payments. Implicit DSR can either be self-directed or directed by an energy management service provider;
The figures below include the explicit and implicit Demand-Side Response
Demand-side response volume
Categories | Total volume [MW]
Max use of 1 hour | 164
Max use of 2 hours | 573
Max use of 4 hours | 570
Max use of 8 hours | 491
No limit | 246
Total shedding capacity | 2044
Total volume [GWh/day in winter period]
Shifting capacity | 0.7
Sources:
Strategic Reserve
Energy Pact

## 3. Balancing capacity
3. Balancing capacity
The table below summarizes the values taken in the framework of the CRM (see Explanatory Note, §2.1.3 for more information).
Volume [MW]
Total FCR | 75
Total FRR | 1104
Total reserve capacity | 1179

## 4. Flow based domains
4. Flow based domains
Elia has developed a flow-based framework which does not rely on historical domains, but instead aims to mimic the operational flow-based capacity calculation workflow.
The framework is based on a zonal model of Europe, the grid model used is based on the TYNDP 2020.
The flow-based perimeter includes the CORE region, with 13-dimensional domains.
Using a framework allows hence to consult on the parameters rather than domains.
The flow-based domains will be illustrated in the final report.
For more information on flow-based please refer to the public consultation on methodology:
4.1.1. Main parameters
Market Parameters | 2026
Flow-based perimeter | CORE
Bidding zones | AS IS
minRAM | See table below
Treatment of external flows | Advanced Hybrid Coupling (AHC)
External constraints | No external constraints
Use of PST** in capacity calculation | For Belgium: 1/2 For other: 1/3
Use of HVDC in flow-based capacity allocation | Only ALEGrO
4.1.2. MinRAM trajectories
Country | 2026
Netherlands | 70
Belgium*
Germany
France
Slovenia
Hungary
Kroatia
Romania
Czechia
Austria
Slovakia
Poland

## 5. Other countries data
5. Sources for other countries
§2.1.5. of the explanatory note further presents the other countries data and its update.
Sources :
Mid-Adequacy Forecast 2020 from ENTSO-E | https://www.entsoe.eu/outlooks/midterm/

## 6. Economic parameters
6. Economic parameters
The prices are based on WEO2020 and are expressed in € 2019 (see §2.1.7. of the explanatory note).
Category | Price
[€/GJ]
Oil | 10.5
Gas | 5.8
Coal | 2
[€/tCO2]
CO2 | 31

## 7. Sensitivities Menu
7. Sensitivities Menu
The proposed sensitivities to add in the reference scenario is further described in §2.2. of the explanatory note.
Sensitivity | Description | Source
French nuclear availability 1 | Decreased French nuclear availability following the reference scenario 2025-26 Lower availability by 2 units on average during winter | Applied in CRM calibration report 2025-26, GAA PLEF 2020
French nuclear availability 2 | Decreased French nuclear availability based on historical figures Lower availability by 4 units on average during winter | Done in Adequacy & Flexibility study (Elia, 2019) and updated with the recent figures
FB CEP rules | Non achievements of the CEP rules for 2026 to reflect the uncertainty on capacity calculation. 50 % RAM instead of 70% | Done in Adequacy & Flexibility study (Elia, 2019)
BE unit at risk | Uncertainties on the future availabilities of turbojets, due to obsolescence and economics | Concerns raised in the public consultation for Adequacy & Flexibility study (Elia, 2021)
BE load stable | In order to reflect a slower growth on the demand side, CREG proposes to integrate a sensitivity where the total demand is equal to the one considered in the 2025-26 calibration report 88.9 TWh instead of 90.2 TWh | Input from CREG in the concertation meeting

## 8. Preselected capacity types
8. Preselected capacity types
The preselected capacity types have the characteristics described in the tabel below. See §3.1 of the explanatory note for further information.
Category | Associated technology | Volume Calculation | Marginal Price Calculation
Type 1 - Semi-baseload | CCGT, CHP | Add new CCGT | Marginal price of a new CCGT
Type 2 - Peakers 1 | OCGT | Add new OCGT | Marginal price of a new OCGT
Type 3 - Peakers 2 | IC engines | Add new IC engines | Marginal price of a new IC engines
Type 4 - DSR | DSR | Add weighted average of existing DSR categories | Weighted average of existing DSR categories

## 9. Scenarios post DY
9. Scenarios post-delivery period choice
Sources of scenarios for periods after the delivery period in order to calculate the market revenues (§3.2 of the explanatory note for further details).
Year | Source
2028 | Adequacy and flexibility study 2022-2032, Elia 2021
2030 | Adequacy and flexibility study 2022-2032, Elia 2021
2035 | Adequacy and flexibility study 2022-2032, Elia 2021
2040 | Adequacy and flexibility study 2022-2032, Elia 2021
Scenario chosen to be as close to the chosen reference in 2026
2026
2030
2035
2040
2028
AdFlex 2028
AdFlex 2030
AdFlex 2032
AdFlex 2032

## 10.1 Technology List
10.1 Intermediate Price Cap - Technology List
The shortlist of technologies is further detailled in §3.3.1. of the explanatory note.
Technology (existing units) | Energy activation duration | Yearly Fixed O&M |  | Source
| hours | [€/kW/year]
|  | low | high
CCGT | / | 29 | 41 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
OCGT | / | 19 | 40 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
Turbojet | / | 23 | 29 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
Pump Storage | 4 | 20 | 40 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
Market response | 4 | 5 | 15 | Public consultation on the methodology, the basis data and scenarios used for the study regarding the adequacy and flexibility needs of the Belgian power system for the period 2022-2032, Elia, 2020

## 10.2 Activation cost avail test
10.2 Intermediate Price Cap - Activation cost of availability test
§3.3.2. of the explanatory note provides further information on activation cost of availability test.
Activation cost, in €/kW-derated/year: | 0,73673€/kWh*0,25h*(1/X) with X the derating factor (in %) associated to the SLA with a 4 hour energy activation constraint
Source: | https://www.elia.be/en/suppliers/supplier/energy-purchases/strategic-reserve-volume-and-prices

## 10.3 Net revenues balancing
10.3 Intermediate Price Cap - Net revenues from balancing services
Net revenues balancing | See explanation note section 3.3.3 for elaboration on general approach regarding the consideration of net revenues from the provision of frequency-related balancing services