## Contents
CRM - Assumptions workbook
Delivery Year 2027-28 - Inputs for Y-4 Auction
This data is provided in the framework of the evaluation of the Belgian CRM calibration. It includes the data required by article 5 of the Royal Decree on volume and parameters http://www.ejustice.just.fgov.be/eli/arrete/2021/04/28/2021041351/justel All the data presented in this excel are targetting the time horizon 2027-28 that will be simulated for the calibration.
1° Data and assumptions for the scenario
1. Generation & Storage
1.1 Generation & Storage summary
1.2 Individually modelled thermal generation
1.3 Storage
1.4 Renewable and thermal without daily schedule
1.5 Forced outage rates
2. Consumption
2.1 Demand
2.2 Demand-Side Response
3. Balancing capacity
4. Flow based domains
5. Other countries data
6. Economic parameters
2° Sensitivities that could be integrated in the reference scenario
7 Sensitivities menu
3° Preselected capacity types
8. Preselected capacity types
4° Net-CONE input data
9. Scenarios post delivery year
5° Intermediate Price Cap
10. Parameters for the IPC
10.1 Technology list
10.2 Revenues parameters

## 1.1 Summary
1.1 Generation & Storage summary
Generation type |  |  | Generation capacity [MW]
Individually modelled non renewable thermal generation |  |  | 9303.9
NU | Nuclear |  | 2077
CCGT | Gas |  | 5461.5
OCGT | Gas |  | 599
CHP | Gas |  | 1008.4
| Oil |  | 158
Profiled thermal non renewable generation |  |  | 1451
Renewable generation |  |  | 17953.4
| Wind |  | 6629
|  | Onshore | 4368
|  | Offshore | 2261
| Photovoltaics |  | 10155
| Hydro RoR |  | 143
| Biomass |  | 692
|  | individually modelled | 68
|  | profiled | 624
| Waste |  | 334.4
|  | individually modelled | 286.4
|  | profiled | 48
Storage |  |  | 2386
| Pumped storage |  | 1305
| Batteries |  | 1081

## 1.2 Ind. mod. thermal gen.
1.2 Individually modelled thermal generation
Owner | Generation unit name | Type | Fuel type | Derating type | Generation capacity [MW] | Comment
Engie - Electrabel | AALST SYRAL GT | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | AALST SYRAL ST | CHP | Gas | CHP, waste & biomass | 5
Engie - Electrabel | AALTER TJ | TJ | Oil | TJ | 18
Engie - Electrabel | AMERCOEUR 1 GT | CCGT-GT | Gas | CCGT | 289
Engie - Electrabel | AMERCOEUR 1 ST | CCGT-ST | Gas | CCGT | 162
Luminus | ANGLEUR TG 31 | GT | Gas | OCGT | 25
Luminus | ANGLEUR TG 32 | GT | Gas | OCGT | 25
Luminus | ANGLEUR TG 41 | GT | Gas | OCGT | 64
Luminus | ANGLEUR TG 42 | GT | Gas | OCGT | 64
Engie - Electrabel | AWIRS 4 | CL | Biomass | CHP, waste & biomass | -
Engie - Electrabel | AWIRS NEW | CCGT | Gas | CCGT | 890 | Contracted in the Y-4 auction for Delivery Period 2025-26 for a duration of 15 years
Engie - Electrabel | BEERSE TJ | TJ | Oil | TJ | 32
Indaver | Beveren 2 Indaver | IS | Waste | CHP, waste & biomass | 21
Indaver | Beveren 3 Indaver | IS | Waste | CHP, waste & biomass | 24
Engie - Electrabel | Beveren Ineos Phenol Chem | CHP | Gas | CHP, waste & biomass | 25.1
Indaver | Beveren Sleco | IS | Waste | CHP, waste & biomass | 41
Biopower | BIOMASSA OOSTENDE | IS | Biomass | CHP, waste & biomass | 18
Biostoom | BIOSTOOM OOSTENDE | IS | Waste | CHP, waste & biomass | 19.4
Borealis | Borealis Kallo Cogen GT_ST | CHP | Gas | CHP, waste & biomass | 32
Engie - Electrabel | CIERREUX TJ | TJ | Oil | TJ | 18
Engie - Electrabel | DOEL 4 | NU | Nuclear | NU | 1039 | Considered operational for the Delivery Period 2027-28
Engie - Electrabel | DROGENBOS GT1 | CCGT-GT | Gas | CCGT | 150
Engie - Electrabel | DROGENBOS GT2 | CCGT-GT | Gas | CCGT | 150
Engie - Electrabel | DROGENBOS ST | CCGT-ST | Gas | CCGT | 160
Euro-silo | Euro-Silo | CHP | Gas | CHP, waste & biomass | 12.9
Indaver | E-wood | IS | Waste | CHP, waste & biomass | 22
Engie - Electrabel | Fluxys Zeebrugge | CHP | Gas | CHP, waste & biomass | 40
Green Power | Greenpower Oostende | IS | Waste | CHP, waste & biomass | 20
Luminus | HAM 31 | GT | Gas | OCGT | 58
Luminus | HAM 32 | GT | Gas | OCGT | 58
Luminus | HAM Gent-GT | CHP | Gas | CHP, waste & biomass | 39
Luminus | HAM Gent-ST | CHP | Gas | CHP, waste & biomass | -
Engie - Electrabel | HERDERSBRUG GT1 | CCGT-GT | Gas | CCGT | 157
Engie - Electrabel | HERDERSBRUG GT2 | CCGT-GT | Gas | CCGT | 156.3
Engie - Electrabel | HERDERSBRUG ST | CCGT-ST | Gas | CCGT | 167
INEOS | INESCO GT1 | CHP | Gas | CHP, waste & biomass | 44.8
INEOS | INESCO GT2 | CHP | Gas | CHP, waste & biomass | 44.8
INEOS | INESCO ST | CHP | Gas | CHP, waste & biomass | 48.5
INTRADEL | INTRADEL | IS | Waste | CHP, waste & biomass | 32
IPALLE | Ipalle THUMAIDE | IS | Waste | CHP, waste & biomass | 34
Engie - Electrabel | ISVAG | IS | Waste | CHP, waste & biomass | 12
Lampiris | IVBO | IS | Waste | CHP, waste & biomass | 16
Engie - Electrabel | IXELLES-VOLTA TJ | TJ | Oil | TJ | 18
Luminus | IZEGEM | CHP | Gas | CHP, waste & biomass | 20
Inovyn | JEMEPPE-SUR-SAMBRE GT1 | CHP | Gas | CHP, waste & biomass | 48
Inovyn | JEMEPPE-SUR-SAMBRE GT2 | CHP | Gas | CHP, waste & biomass | 48
Inovyn | JEMEPPE-SUR-SAMBRE ST | CHP | Gas | CHP, waste & biomass | 10
Engie - Electrabel | KNIPPEGROEN STEG | GT | Gas | OCGT | 305
Lillo Energy | Lillo Degussa GT1 | CHP | Gas | CHP, waste & biomass | 43
Lillo Energy | Lillo Degussa GT2 | CHP | Gas | CHP, waste & biomass | 32
Lillo Energy | Lillo Degussa ST | CHP | Gas | CHP, waste & biomass | 10
Direct Energie | MARCINELLE ENERGIE TGV | CCGT | Gas | CCGT | 413
Engie - Electrabel | MONSANTO LILLO WKK EBL | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | NOORDSCHOTE TJ | TJ | Oil | TJ | 18
Engie - Electrabel | Oorderen Bayer | CHP | Gas | CHP, waste & biomass | 43
Luminus | RINGVAART STEG | CCGT | Gas | CCGT | 385
Engie - Electrabel | RODENHUIZE 4 | CL | Biomass | CHP, waste & biomass | - | Considered out of the market as of 2023
Engie - Electrabel | SAINT-GHISLAIN STEG | CCGT | Gas | CCGT | 386 | Capacity increases from 350 MW to 386 MW
Engie - Electrabel | SAPPI LANAKEN GT | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | Schaerbeek SIOMAB 1 | IS | Waste | CHP, waste & biomass | 15
Engie - Electrabel | Schaerbeek SIOMAB 2 | IS | Waste | CHP, waste & biomass | 15
Engie - Electrabel | Schaerbeek SIOMAB 3 | IS | Waste | CHP, waste & biomass | 15
EXXONMOBIL | SCHELDELAAN EXXONMOBIL | CHP | Gas | CHP, waste & biomass | 140
Luminus | SERAING TG1 | CCGT-GT | Gas | CCGT | 150
Luminus | SERAING TG2 | CCGT-GT | Gas | CCGT | 150
Luminus | SERAING TGV | CCGT-ST | Gas | CCGT | - | Considered out of the market as of November 2025
Luminus | SERAING NEW | CCGT | Gas | CCGT | 885 | Contracted in the Y-4 auction for Delivery Period 2025-26 for a duration of 15 years
STORA | STORA LANGERBRUGGE CHP 1 | CHP | Biomass | CHP, waste & biomass | 10
STORA | STORA LANGERBRUGGE CHP 2 | CHP | Biomass | CHP, waste & biomass | 40
Taminco | TAMINCO GENT CHP | CHP | Gas | CHP, waste & biomass | 6.3
Engie - Electrabel | Tihange 3 | NU | Nuclear | NU | 1038 | Considered operational for the Delivery Period 2027-28
T-Power | T-POWER | CCGT | Gas | CCGT | 425
Engie - Electrabel | VILVOORDE GT | CCGT-GT | Gas | CCGT | -
TOTAL | WILMARSDONK TOTAL GT1 | CHP | Gas | CHP, waste & biomass | 43
TOTAL | WILMARSDONK TOTAL GT2 | CHP | Gas | CHP, waste & biomass | 43
TOTAL | WILMARSDONK TOTAL GT3 | CHP | Gas | CHP, waste & biomass | 43
Zandvliet Power NV | ZANDVLIET POWER | CCGT | Gas | CCGT | 386.2
Engie - Electrabel | ZEDELGEM TJ | TJ | Oil | TJ | 18
Engie - Electrabel | ZEEBRUGGE TJ | TJ | Oil | TJ | 18
Engie - Electrabel | ZELZATE TJ | TJ | Oil | TJ | 18
Engie - Electrabel | Zwijndrecht Lanxess GT | CHP | Gas | CHP, waste & biomass | 43
Engie - Electrabel | Zwijndrecht Lanxess ST | CHP | Gas | CHP, waste & biomass | 15
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit

## 1.3 Storage
1.3 Storage
1.3.1 Pumped-Storage
| BE Pumped-Storage facilities |  | Reservoir Volume [MWh]
| Storage reservoir |  | 6150
| Storage reservoir derating (black-start services) |  | 500
| Available storage for economical dispatch |  | 5650
| Unit name |  | Turbining capacity [MW]
| Total capacity |  | 1305
| Coo 1-6 |  | 1161
| Platte Taille 1-4 |  | 144
1.3.2 Batteries
a) Definition in the ERAA methodology regarding batteries:
In-the-market batteries, which are large-scale battery capacities that are traded in day-ahead and intraday markets. In-the-market batteries shall be modelled similarly to pumped-hydro storage and shall be subject to the following constraints: maximum power, maximum energy storage, state of charge, charging/discharging efficiency; Out-of-market batteries, which represent small-scale batteries typically managed behind the meter. Out-of-market batteries shall be modelled as peak-shaving units based on predefined peak-reduction ratios, which are a direct input to the demand prediction process
Three categories are considered for "batteries" in this study: large scale batteries, small scale batteries and Vehicle-to-Grid (V2G).
The small scale batteries are assumed to be managed behind the meter and are considered for this reason in the "out-of-market" category.
The large scale batteries are assumed to participate to the electricity market and are considered for this reason in "in-the-market" category.
The capacity for V2G is shared between "in-the-market" and "out-of-market" categories as a part was assumed reacting to market prices and another to local behind the meter optimization. This share evolves with time as described in the table below.
Regarding the energy content of the different "batteries" category, small-scale batteries and V2G have respectively an energy content of 3 and 4h. For large-scale batteries, the energy content is shared between 2h and 4h batteries with a 30/70 percentage.
| Total capacity [MW] |  | 1081
| Capacity [MW] | Large scale storage ("in-the-market") | 458
|  | Small scale storage ("out-of-market") | 381
|  | Vehicule-to-Grid (V2G) | 242
|  | V2G "in-the-market" | 56
|  | V2G "out-of-market" | 186
| Reservoir volume [MWh] | Large scale storage ("in-the-market") | 1557.2
| Reservoir volume [MWh] | Small scale storage ("out-of-market") | 1143
|  | Vehicule-to-grid | 968
|  | V2G "in-the-market" | 224
|  | V2G "out-of-market" | 744

## 1.4 Renewable and profiled
1.4 Renewable energy sources and thermal without daily schedule units
Generation type |  | Generation capacity [MW]
Renewable energy sources |  | 16927
| Wind | 6629
| Wind onshore | 4368
| Wind offshore | 2261
| Photovoltaics | 10155
| Hydro RoR | 143
profiled thermal without daily schedule units |  | 2123
| Gas CHP - wihout daily schedule | 1451
| Biomass - wihout daily schedule | 624
| Waste - wihout daily schedule | 48

## 1.5 Forced outage rates
1.5 Forced outage rates
Average forced outage rate over 2012-2021
CCGT | 7%
GT | 7.407%
TJ | 3.5%
CHP, waste & biomass | 6.7%
Pumped storage | 4.3%
HVDC link | 6%
| 'Technical' forced outage rate over 2012-2021 | 'Long-lasting' forced outage rate over 2012-2021 | Planned outage rate during winter periods over 2012-2021
Nuclear | 4% | 16.5% | 8.1%
Sources:
Elia (2012-2021)
ENTSO-E Transparency platform (2015-2021) where available
MAF Study

## 2.1 Demand
2.1 Demand
|  | Total demand [TWh] | Normalised total demand [TWh]
historical | 2020 | 81 | 82.1
| 2021 | 84.2 | 84.4
Total demand forecasted | 2027 |  | 94.6
Sources:
The total electricity demand for Belgium is based on the tool developped by Climact in the scope of the strategic reserve study where the methodology used is described in the following report:
https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2020/20200603_total-electricity-demand-forecasting_en.pdf
The macro-economic input data used in the tool are based on the report published by Federal Plan Bureau on June 2021:
https://www.plan.be/publications/publication-2130-fr-perspectives_economiques_2021_2026_version_de_juin_2021
The latest presentation from Climact is available here:
https://www.elia.be/en/users-group/plenary-meetings/20210928-meeting
The assumptions for electrification are derived from latest national and European ambitions (FitFor55, REPowerEU)
Assumptions:
2027
Number of Equivalent Electric Vehicles |  | 850000
Number of Heat Pumps |  | 250000
Daily natural vs V1G EV profiles based on AdeqFlex 21, Figure 3-8 but updated
V1G profile share proposal = 41%

## 2.2 Demand-Side Response
2.2 Demand-Side Response
a) Definition in the ERAA methodology regarding Demand-Side Response (DSR):
'explicit demand-side response’ (explicit DSR) means the change of electric demand pursuant to an accepted offer to sell demand reduction or increase in an organised market, either directly or through aggregation. Explicit DSR may consist of either foregone or time-shifted demand;
‘implicit demand-side response’ (implicit DSR) means the change of demand by final customers from their normal or current consumption patterns, in response to time-variable electricity prices or incentive payments. Implicit DSR can either be self-directed or directed by an energy management service provider;
The figures below include the explicit and implicit Demand-Side Response
Demand-side response volume
Categories | Total volume [MW]
Max use of 1 hour | 174.5912
Max use of 2 hours | 610.136
Max use of 4 hours | 657
Max use of 8 hours | 523.1735
No limit | 261.5537
Total shedding capacity | 2226.4543
Total volume [MWh/day in winter period]
Shifting capacity | 1000
Sources:
Energy Pact
Adequacy & Flexibility study 2022-2032 (Elia, 2021)
Additional electrification ambition based on recent national and European measures (REPowerEU, FF55)

## 3. Balancing capacity
3. Balancing capacity
Volume [MW]
Total FCR | 75
Total FRR | 1175
Total reserve capacity | 1250

## 4. Flow based domains
4. Flow based domains
Elia has developed a flow-based framework which does not rely on historical domains, but instead aims to mimic the operational flow-based capacity calculation workflow.
The framework is based on a zonal model of Europe, the grid model used is based on the TYNDP 2020.
The flow-based perimeter includes the CORE region, with 13-dimensional domains.
Using a framework allows hence to consult on the parameters rather than domains.
The flow-based domains will be illustrated in the final report.
For more information on flow-based please refer to the public consultation on methodology:
4.1.1. Main parameters
Market Parameters | 2027
Flow-based perimeter | CORE
Bidding zones | AS IS
minRAM | See table below
Treatment of external flows | Advanced Hybrid Coupling (AHC)
External constraints | No external constraints
Use of PST** in capacity calculation | For Belgium: 1/2 For other: 1/3
Use of HVDC in flow-based capacity allocation | Only ALEGrO
4.1.2. MinRAM trajectories
Country | 2027
Netherlands | 70
Belgium*
Germany
France
Slovenia
Hungary
Kroatia
Romania
Czechia
Austria
Slovakia
Poland

## 5. Other countries data
5. Sources for other countries
Sources :
European Resource Adequacy Assessment 2021 from ENTSO-E |  |  | https://www.entsoe.eu/outlooks/eraa/
Updates proposed :
Countries | Proposed Updates
| Lignite/Coal [MW] | Wind Onshore [MW] | Wind Offshore [MW] | Solar [MW] | Demand [TWh/y]
DE | 10700 | 74300 | 22000 | 137200 | 623
FR | 0 | 24100 | 6200 | 44000 | 482
NL | 2671 | 7800 | 11500 | 26900 | 143
GB | 0 | 24200 | 36300 | 31900 | 306
Total
The sources for the proposed updates are presented in the explanatory note.

## 6. Economic parameters
6. Economic parameters
The prices are based on "Announced Pledges" scenario from WEO2021 and are expressed in € 2020.
Category | Price
[€ 2020/MWh]
Oil | 46.4
Gas | 24.4
Coal | 12.7
[€ 2020/tCO2]
CO2 | 97.3

## 7. Proposed sensitivities
7. Proposed sensitivities
Sensitivity | Description
French nuclear availability - 2 units | Decreased French nuclear availability in line with the reference scenario 2025-26 and 2026-27 Lower availability by 2 units on average during winter
French nuclear availability - 4 units | Decreased French nuclear availability based on historical figures Lower availability by 4 units on average during winter
French nuclear availability - 6 units | Decreased French nuclear availability based on historical figures Lower availability by 6 units on average during winter
French nuclear availability - 8 units | Decreased French nuclear availability based on historical figures Lower availability by 8 units on average during winter
FB CEP rules | Non achievements of the CEP rules for 2027 to reflect the uncertainty on capacity calculation. Fixed RAM 70% instead of 70% minRAM
TJ closure | Closure of turbojets due to possible CO2 threshold -158 MW
OCGT closure | Closure of old OCGT due to possible CO2 threshold -511 MW
High Prices | Maintain of high prices in Europe Higher fuel costs (35,4 €2020/MWh for gas and 17,1 €2020/MWh for coal)
Low Prices | Back to prices pre-crisis in Europe Lower fuel costs (19,8 €2020/MWh for gas and 8,6 €2020/MWh for coal)
Lower demand | Lower demand in Belgium due to high prices Lower yearly consumption due to high electricity prices (already integrated in the high prices sensitivity)

## 8. Preselected capacity types
8. Preselected capacity types
The preselected capacity types have the characteristics described in the tabel below.
Category | Associated technology | Volume Calculation | Marginal Price Calculation | CAPEX | FOM | Economic lifetime
|  |  |  | [€ 2020/kW] | [€ 2020/kW] | [y]
Type 1 - Semi-baseload | CCGT, CHP | Add new CCGT | Marginal price of a new CCGT | 600 | 25 | 20
Type 2 - Peakers 1 | OCGT | Add new OCGT | Marginal price of a new OCGT | 400 | 20 | 20
Type 3 - Peakers 2 | IC engines | Add new IC engines | Marginal price of a new IC engines | 300 | 15 | 15
Type 4 - Batteries | Large-scale bat. | Add new Large-scale batteries | / | 250 | 15 | 15
Type 5 - DSR | DSR | Add weighted average of existing DSR categories | Weighted average of existing DSR categories | see below

## 9. Scenarios post DY
9. Scenarios post-delivery period choice
Sources of scenarios for periods after the delivery period in order to calculate the market revenues.
Scenario chosen to be as close to the chosen reference in 2026
2027
2030
2040
2028
AdFlex 21
AdFlex 21 (2032 Scenario)
2032

## 10.1 IPC - Technology List
10.1 Intermediate Price Cap - Technology List
Technology (existing units) | Energy activation duration | Yearly Fixed O&M |  |  | Source
| hours | [€/kW/year]
|  | low | mid | high
CCGT | / | 29 | 30 | 41 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
OCGT | / | 19 | 19 | 40 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
Turbojet | / | 23 | 29 | 29 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
Pump Storage | 4 | 20 | 29 | 40 | Peer review of annual fixed costs for Belgian CRM, AFRY, 2020
Market response | 4 | 5 | 10 | 15 | Public consultation on the methodology, the basis data and scenarios used for the study regarding the adequacy and flexibility needs of the Belgian power system for the period 2022-2032, Elia, 2020
WACC | 5.53%
Hurdle Premium | Annex 1, https://www.ejustice.just.fgov.be/eli/arrete/2021/04/28/2021041351/justel#LNK0008

## 10.2 IPC - Revenues parameters
10.2 Intermediate Price Cap - Input parameters for revenues
Input parameters for market revenues
Technologies | Efficiency [%] |  |  | VOM [€ 2020/MWh]
| low | mid | high | low | mid | high
CCGT | 50 | 54 | 58 | 2 | 2 | 2
OCGT | 35 | 40 | 44 | 11 | 11 | 11
Turbojet | 21 | 28 | 35 | 3,3 | 3,3 | 3,3
Activation cost of availability test
Activation cost, in €/kW-derated/year: |  | 0,73673€/kWh*0,25h*(1/X) with X the derating factor (in %) associated to the SLA with a 4 hour energy activation constraint
Source: |  | https://www.elia.be/en/suppliers/supplier/energy-purchases/strategic-reserve-volume-and-prices