## Contents
CRM - Assumptions workbook
Inputs for the scenario proposal for auction Y-1 (delivery year 2025-2026) and for auction Y-4 (delivery year 2028-2029)
This data is provided in the framework of the evaluation of the Belgian CRM calibration. It includes the data required by article 5 of the Royal Decree on volume and parameters http://www.ejustice.just.fgov.be/eli/arrete/2021/04/28/2021041351/justel All the data presented in this Excel are targetting the time horizons 2025-2026 and 2028-2029 that are proposed as basis for the simulations used for the calibration of the auction Y-1 and Y-4.
1° Data and assumptions for the scenario
1. Generation & Storage
1.1 Generation & Storage summary
1.2 Individually modelled thermal generation
1.3 Storage
1.4 Renewable and thermal without daily schedule
1.5 Forced outage rates
2. Consumption
2.1 Demand
2.2 Demand-Side Response
3. Balancing capacity
4. Flow based domains
5. Other countries data
6. Economic parameters
2° Sensitivities that could be integrated in the reference scenario
7 Sensitivities menu
3° Preselected capacity types
8. Preselected capacity types
4° Net-CONE input data
9. Scenarios post delivery year
5° Intermediate Price Cap
10. Parameters for the IPC
10.1 Technology list
10.2 Revenues parameters

## 1.1 Summary
1.1 Generation & Storage summary
Generation type |  |  | Generation capacity [MW]
|  |  | 2025-2026 | 2028-2029
Individually modelled non renewable thermal generation |  |  | 7241.7 | 9318.7
NU | Nuclear |  | 0 | 2077
CCGT | Gas |  | 5494.3 | 5494.3
OCGT | Gas |  | 599 | 599
CHP | Gas |  | 1008.4 | 1008.4
TJ | Oil |  | 140 | 140
Profiled thermal non renewable generation |  |  | 1499 | 1594
Renewable generation |  |  | 17365.4 | 21023.4
| Wind |  | 6189 | 7179
|  | Onshore | 3928 | 4918
|  | Offshore | 2261 | 2261
| Photovoltaics |  | 10090 | 12730
| Hydro RoR |  | 137 | 145
| Biomass |  | 615 | 635
|  | individually modelled | 68 | 68
|  | profiled | 547 | 567
| Waste |  | 334.4 | 334.4
|  | individually modelled | 286.4 | 286.4
|  | profiled | 48 | 48
Storage |  |  | 2016 | 2087
| Pumped storage |  | 1305 | 1305
| Large and small scale Batteries |  | 711 | 782

## 1.2 Ind. mod. thermal gen.
1.2 Individually modelled thermal generation
Owner | Generation unit name | Type | Fuel type | Derating type | Net generation capacity [MW] | Comment | Situation at end of the given year
[7 empty] | 2025-2026 | 2028-2029
Engie - Electrabel | AALST SYRAL GT | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Engie - Electrabel | AALST SYRAL ST | CHP | Gas | CHP, waste & biomass | 5 |  | yes | yes
Engie - Electrabel | AALTER TJ | TJ | Oil | TJ | 18 |  | yes | yes
Engie - Electrabel | AMERCOEUR 1 GT | CCGT-GT | Gas | CCGT | 289 |  | yes | yes
Engie - Electrabel | AMERCOEUR 1 ST | CCGT-ST | Gas | CCGT | 162 |  | yes | yes
Luminus | ANGLEUR TG 31 | GT | Gas | OCGT | 25 |  | yes | yes
Luminus | ANGLEUR TG 32 | GT | Gas | OCGT | 25 |  | yes | yes
Luminus | ANGLEUR TG 41 | GT | Gas | OCGT | 64 |  | yes | yes
Luminus | ANGLEUR TG 42 | GT | Gas | OCGT | 64 |  | yes | yes
Engie - Electrabel | BEERSE TJ | TJ | Oil | TJ | 32 |  | yes | yes
Indaver | Beveren 2 Indaver | IS | Waste | CHP, waste & biomass | 21 |  | yes | yes
Indaver | Beveren 3 Indaver | IS | Waste | CHP, waste & biomass | 24 |  | yes | yes
Indaver | Beveren Ineos Phenol Chem | CHP | Gas | CHP, waste & biomass | 25.1 |  | yes | yes
Indaver | Beveren Sleco | IS | Waste | CHP, waste & biomass | 41 |  | yes | yes
Biopower | BIOMASSA OOSTENDE | IS | Biomass | CHP, waste & biomass | 18 |  | yes | yes
Biostoom | BIOSTOOM OOSTENDE | IS | Waste | CHP, waste & biomass | 19.4 |  | yes | yes
Borealis | Borealis Kallo Cogen GT_ST | CHP | Gas | CHP, waste & biomass | 32 | Commissioning date expected - mid-2024 (01/07/2024 considered) https://www.spglobal.com/commodityinsights/en/market-insights/latest-news/petrochemicals/090122-pdh-project-in-belgium-delayed-to-mid-2024-as-borealis-retenders-construction-contracts | yes | yes
Engie - Electrabel | CIERREUX TJ | TJ | Oil | TJ | 18 |  | yes | yes
Engie - Electrabel | DOEL 1 | NU | Nuclear | NU | 445 | Decommissioning: 15/02/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du | no | no
Engie - Electrabel | DOEL 2 | NU | Nuclear | NU | 445 | Decommissioning: 01/12/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du | no | no
Engie - Electrabel | DOEL 3 | NU | Nuclear | NU | 1006 | Decommissioning: 01/10/2022 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du | no | no
Engie - Electrabel | DOEL 4 | NU | Nuclear | NU | 1039 | Lifetime extension - Considered operational for winter 26-27 | no | yes
Engie - Electrabel | DROGENBOS GT1 | CCGT-GT | Gas | CCGT | 150 |  | yes | yes
Engie - Electrabel | DROGENBOS GT2 | CCGT-GT | Gas | CCGT | 150 |  | yes | yes
Engie - Electrabel | DROGENBOS ST | CCGT-ST | Gas | CCGT | 160 |  | yes | yes
Euro-silo | Euro-Silo | CHP | Gas | CHP, waste & biomass | 12.9 |  | yes | yes
Indaver | E-wood | IS | Waste | CHP, waste & biomass | 22 |  | yes | yes
Engie - Electrabel | Flémalle NEW | CCGT | Gas | CCGT | 890 | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results | yes | yes
Engie - Electrabel | Fluxys Zeebrugge | CHP | Gas | CHP, waste & biomass | 40 |  | yes | yes
Green Power | Greenpower Oostende | IS | Waste | CHP, waste & biomass | 20 |  | yes | yes
Luminus | HAM 31 | GT | Gas | OCGT | 58 |  | yes | yes
Luminus | HAM 32 | GT | Gas | OCGT | 58 |  | yes | yes
Luminus | HAM Gent-GT | CHP | Gas | CHP, waste & biomass | 39 |  | yes | yes
Luminus | HAM Gent-ST | CHP | Gas | CHP, waste & biomass | -
Engie - Electrabel | HERDERSBRUG GT1 | CCGT-GT | Gas | CCGT | 157 |  | yes | yes
Engie - Electrabel | HERDERSBRUG GT2 | CCGT-GT | Gas | CCGT | 156.3 |  | yes | yes
Engie - Electrabel | HERDERSBRUG ST | CCGT-ST | Gas | CCGT | 167 |  | yes | yes
INEOS | INESCO GT1 | CHP | Gas | CHP, waste & biomass | 44.8 |  | yes | yes
INEOS | INESCO GT2 | CHP | Gas | CHP, waste & biomass | 44.8 |  | yes | yes
INEOS | INESCO ST | CHP | Gas | CHP, waste & biomass | 48.5 |  | yes | yes
INTRADEL | INTRADEL | IS | Waste | CHP, waste & biomass | 32 |  | yes | yes
IPALLE | Ipalle THUMAIDE | IS | Waste | CHP, waste & biomass | 34 |  | yes | yes
Engie - Electrabel | ISVAG | IS | Waste | CHP, waste & biomass | 12 |  | yes | yes
Lampiris | IVBO | IS | Waste | CHP, waste & biomass | 16 |  | yes | yes
Luminus | IZEGEM | CHP | Gas | CHP, waste & biomass | 20 |  | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE GT1 | CHP | Gas | CHP, waste & biomass | 48 |  | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE GT2 | CHP | Gas | CHP, waste & biomass | 48 |  | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE ST | CHP | Gas | CHP, waste & biomass | 10 |  | yes | yes
Engie - Electrabel | KNIPPEGROEN STEG | GT | Gas | OCGT | 305 |  | yes | yes
Lillo Energy | Lillo Degussa GT1 | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Lillo Energy | Lillo Degussa GT2 | CHP | Gas | CHP, waste & biomass | 32 |  | yes | yes
Lillo Energy | Lillo Degussa ST | CHP | Gas | CHP, waste & biomass | 10 |  | yes | yes
Direct Energie | MARCINELLE ENERGIE TGV | CCGT | Gas | CCGT | 413 |  | yes | yes
Engie - Electrabel | MONSANTO LILLO WKK EBL | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Engie - Electrabel | NOORDSCHOTE TJ | TJ | Oil | TJ | 18 |  | yes | yes
Engie - Electrabel | Oorderen Bayer | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Luminus | RINGVAART STEG | CCGT | Gas | CCGT | 385 |  | yes | yes
Engie - Electrabel | RODENHUIZE 4 | CL | Biomass | CHP, waste & biomass | - | Considered out of the market as of 2023 (back of Knippegroen according to REMIT) | no | no
Engie - Electrabel | SAINT-GHISLAIN STEG | CCGT | Gas | CCGT | 386 | Capacity increases from 350 MW to 386 MW | yes | yes
Engie - Electrabel | SAPPI LANAKEN GT | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Centre de Tri | Schaerbeek SIOMAB 1 | IS | Waste | CHP, waste & biomass | 15 |  | yes | yes
Centre de Tri | Schaerbeek SIOMAB 2 | IS | Waste | CHP, waste & biomass | 15 |  | yes | yes
Centre de Tri | Schaerbeek SIOMAB 3 | IS | Waste | CHP, waste & biomass | 15 |  | yes | yes
EXXONMOBIL | SCHELDELAAN EXXONMOBIL | CHP | Gas | CHP, waste & biomass | 140 |  | yes | yes
Luminus | SERAING NEW | CCGT | Gas | CCGT | 885 | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results | yes | yes
Luminus | SERAING TG1 | CCGT-GT | Gas | CCGT | 150 |  | yes | yes
Luminus | SERAING TG2 | CCGT-GT | Gas | CCGT | 150 |  | yes | yes
Luminus | SERAING ST | CCGT-ST | Gas | CCGT | 170 | Art. 4bis - Decommissioning date: 18/04/2024 - https://economie.fgov.be/sites/default/files/Files/Energy/tijdelijke-buitenwerkingstelling-stoomturbinesteg-centrale-seraing.pdf | no | no
STORA | STORA LANGERBRUGGE CHP 1 | CHP | Biomass | CHP, waste & biomass | 10 |  | yes | yes
STORA | STORA LANGERBRUGGE CHP 2 | CHP | Biomass | CHP, waste & biomass | 40 |  | yes | yes
Taminco | TAMINCO GENT CHP | CHP | Gas | CHP, waste & biomass | 6.3 |  | yes | yes
Engie - Electrabel | TIHANGE 1N | NU | Nuclear | NU | 481 | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du | no | no
Engie - Electrabel | TIHANGE 1S | NU | Nuclear | NU | 481 | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du | no | no
Engie - Electrabel | TIHANGE 2 | NU | Nuclear | NU | 1008 | Decommissioning: 01/02/2023 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du | no | no
Engie - Electrabel | Tihange 3 | NU | Nuclear | NU | 1038 | Considered operational for the Delivery Period 2027-28 | no | yes
T-Power | T-POWER | CCGT | Gas | CCGT | 425 |  | yes | yes
Engie - Electrabel | TURBOJET VOLTA | TJ | Oil | TJ | 18 | Art. 4bis - Decommissioning date: 26/08/2023 - https://economie.fgov.be/sites/default/files/Files/Energy/22-54-EBL-FOD-N-Mahieu-fermeture-TJ-VOLTA-Art4-%20GHS-signed.pdf | no | no
Engie - Electrabel | VILVOORDE GT | CCGT-GT | Gas | CCGT | 255 | Art. 4bis - Decommissioning date: 31/10/2025 - https://economie.fgov.be/sites/default/files/Files/Energy/21-34-EBL-SPF-mise-a-l-arret-definitive-central-de-Vilvoorde.pdf. Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf | no | no
Engie - Electrabel | VILVOORDE ST | CCGT-ST | Gas | CCGT | 105 | Based on REMIT information, decommissioning 01/04/2023. Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf | no | no
TOTAL | WILMARSDONK TOTAL GT1 | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
TOTAL | WILMARSDONK TOTAL GT2 | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
TOTAL | WILMARSDONK TOTAL GT3 | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Zandvliet Power NV | ZANDVLIET POWER | CCGT | Gas | CCGT | 419 | The nominal capacity is considered as of 11/2024 | yes | yes
Engie - Electrabel | ZEDELGEM TJ | TJ | Oil | TJ | 18 |  | yes | yes
Engie - Electrabel | ZEEBRUGGE TJ | TJ | Oil | TJ | 18 |  | yes | yes
Engie - Electrabel | ZELZATE TJ | TJ | Oil | TJ | 18 |  | yes | yes
Engie - Electrabel | Zwijndrecht Lanxess GT | CHP | Gas | CHP, waste & biomass | 43 |  | yes | yes
Engie - Electrabel | Zwijndrecht Lanxess ST | CHP | Gas | CHP, waste & biomass | 15 |  | yes | yes
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit

## 1.3 Storage
1.3 Storage
1.3.1 Pumped-Storage
| BE Pumped-Storage facilities | Reservoir Volume [MWh]
|  | 2025-2026 | 2028-2029
| Storage reservoir | 6300 | 6300
| Storage reservoir derating (black-start services) | 500 | 500
| Available storage for economical dispatch | 5800 | 5800
| BE Pumped-Storage facilities | Turbining capacity [MW]
|  | 2025-2026 | 2028-2029
| Total capacity | 1305 | 1305
| Coo 1-6 | 1161 | 1161
| Platte Taille 1-4 | 144 | 144
1.3.2 Batteries
a) Definition in the ERAA methodology regarding batteries:
In-the-market batteries, which are large-scale battery capacities that are traded in day-ahead and intraday markets. In-the-market batteries shall be modelled similarly to pumped-hydro storage and shall be subject to the following constraints: maximum power, maximum energy storage, state of charge, charging/discharging efficiency; Out-of-market batteries, which represent small-scale batteries typically managed behind the meter. Out-of-market batteries shall be modelled as peak-shaving units based on predefined peak-reduction ratios, which are a direct input to the demand prediction process
Two categories are considered for "batteries" in this study: large scale batteries and small scale batteries.
The small scale batteries are categorized into two groups: those managed behind the meter, which fall under the "out-of-market" category, and those assumed to participate in the electricity market, which fall under the "in-the-market" category.
The large scale batteries are assumed to participate to the electricity market and are considered for this reason in "in-the-market" category.
For large-scale batteries, the energy content is shared between 2h and 4h batteries.
| Batteries - Capacity in reference scenario | Capacity [MW]
|  | 2025-2026 | 2028-2029
| Total | 711 | 782
| Small scale storage ("out-of-market") | 192 | 91
| Small scale storage ("in-the-market") | 192 | 364
| Large scale storage ("in-the-market") | 327 | 327
| Batteries - Reservoir volume in reference scenario | Reservoir volume [MWh]
|  | 2025-2026 | 2028-2029
| Total | 1873 | 2015
| Small scale storage ("out-of-market") | 384 | 182
| Small scale storage ("in-the-market") | 384 | 728
| Large scale storage ("in-the-market") | 1105 | 1105
| Large scale batteries - Potentially added during calibration | 2025-2026 | 2028-2029
| Large scale storage ("in-the-market") - Capacity [MW] | 626 | 1868
| Large scale storage ("in-the-market") - Reservoir volume [MWh] | 2504 | 7472

## 1.4 Renewable and profiled
1.4 Renewable energy sources and thermal without daily schedule units
Generation type |  | Generation capacity [MW]
|  | 2025-2026 | 2028-2029
Renewable energy sources |  | 16416 | 20054
| Wind | 6189 | 7179
| Wind onshore | 3928 | 4918
| Wind offshore | 2261 | 2261
| Photovoltaics | 10090 | 12730
| Hydro RoR | 137 | 145
profiled thermal without daily schedule units |  | 2094 | 2209
| Gas CHP - wihout daily schedule | 1499 | 1594
| Biomass - wihout daily schedule | 547 | 567
| Waste - wihout daily schedule | 48 | 48

## 1.5 Forced outage rates
1.5 Forced outage rates
Category | Number of FO per year | Average FO rate [%] | Average duration of FO rate [hours]
Nuclear | 1.3* | 20.5% | 199 hours* [around 8 days]
CCGT | 9.4 | 5.5% | 110 hours [ around 5 days]
OCGT | 9.2 | 8.2% | 221 hours [around 9 days]
TJ | 3.2 | 9.8% | 130 hours [around5 days]
CHP, waste, biomass | 2.9 | 6.4% | 111 hours [around 5 days]
Pumped Storage | 5.8 | 2.9% | 46 hours [around 2 day]
Batteries | / | 2.0%*** | /
DC links | 1.9 | 6.7% | 158 hours [around 7 days]
* Only considering technical forced outages.
** Also considering long-lasting forced outages
*** Regarding batteries, the forced outage rate is considered in the models by applying a derating factor on the installed capacity
Sources:
Forced outage rates have been calculated in a study performed by N-Side, which was part of the public consultation of AdeqFlex 23. For pumped-storage and batteries, the forced outage rates were updated based on feedback received during AdeqFlex 23 public consultation.

## 2.1 Demand
2.1 Demand
|  | Total demand [TWh] | Normalised total demand [TWh]
historical | 2021 | 84.5 | 84.7
| 2022 | 81.7 | 82.9
Total demand forecasted | 2025 |  | 88.7
| 2028 |  | 104.4
Sources:
AdeqFlex 23 normalised total demand of the base trajectory for 2025 and 2028. And includes:
Organic load: calculated by Climact for AdeqFlex 23 based on parameters in the next sheet
Additional electrification of EV and HP: trajectories of AdeqFlex 23 as detailed below and included by Climact as detailed in the next sheet
Additional electrification of industry: AdeqFlex 23 trajectories based on 'Powering Industry to net zero' strudy
Grid losses
Assumptions:
Electric Vehicles* |  | 2025 | 2028
Passengers Cars BEV [thousand] |  | 400 | 1170
Passengers Cars PHEV [thousand] |  | 430 | 400
LDV freight BEV [thousand] |  | 28 | 90
LDV freight PHEV [thousand] |  | 10 | 24
HDV freight BEV [thousand] |  | 0 | 1
Busses BEV [thousand] |  | 2 | 4
Heat Pumps* |  | 2025 | 2028
Residential HP [thousand] |  | 815 | 1061
Tertiary HP [thousand] |  | 70 | 114
Electrification |  | 2025 | 2028
Additional electrification in industry [TWh] |  | 2.3 | 9.2
Additional electrification due to data centers [TWh] |  | 0.8 | 2
*The flexibility consideration for the Electric Vehicles and the Heat Pumps are detailed in the explanatory note.

## 2.2 Demand - Climact parameters
Last available values for the variables used in the modelling exercise
Category | Variable | Unit | Type of value | Source | Driver | Year/value
Category | [5 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Growth rate of added value per sector | Intermediate goods | % | External | Bureau Fédéral du Plan, Perspectives économiques 2022-2027 - juin 2022. For 2028, the services sector (everything excepted intermediate, capital and consumer goods) added value growth rate has been obtained by extrapolating 2022-2027 figures for the services sector as a whole. For industry sectors ( intermediate, capital and consumer goods), the growth rate has been considered to be equal to 0 to model a stationnary industry output. See accompanying document for justification | N/A | 1.8% | 1.4% | 2.2% | 1.8% | 1.7% | 1.8% | 0%
| Capital goods |  |  |  |  | 4.3% | 1.2% | 1.2% | 0.7% | 0.6% | 1% | 0%
| Consumer goods |  |  |  |  | 2.1% | 0.6% | 0.9% | 0.5% | 0.6% | 0.7% | 0%
| Transport and communication |  |  |  |  | 6.2% | 1.7% | 1.9% | 1.6% | 1.6% | 1.8% | 1.4%
| Trade and horeca |  |  |  |  | 2.2% | 1.4% | 1.4% | 1.2% | 1.2% | 1.2% | 1.4%
| Credit and insurance |  |  |  |  | 0.5% | 1.3% | 1.6% | 1.3% | 1.2% | 1.3% | 1.4%
| Health and social work (incl. service vouchers) |  |  |  |  | 3% | 0.6% | 0.9% | 1.3% | 1.2% | 1.3% | 1.4%
| Other market services (incl. service cheques and FTA jobs) |  |  |  |  | 4.5% | 1.7% | 2.3% | 2.1% | 2.1% | 2.2% | 1.4%
| Non-market services |  |  |  |  | 0.2% | 0.9% | 0.7% | 0.6% | 0.7% | 0.7% | 1.4%
Disposable income | Growth rate of gross personal disposable income | % | External | Bureau Fédéral du Plan, Perspectives économiques 2022-2027 - juin 2022. 2028 value has been obtained by extrapolating 2020-2027 values | N/A | 0.5% | 2.3% | 1.6% | 1.2% | 1.4% | 1.4% | 0.6%
| Freight transport demand | Gtkm/year | Computed | N/A | Macro-eco - Growth rate of the total industry added value | 74.76 | 75.43 | 76.3 | 77.07 | 77.74 | 78.51 | 79.28
| Electricity consumption for cars and vans | TWh/year | External | Elia trajectories for the AdeqFlex 23 study | N/A | 0.48714 | 0.77881 | 1.2322 | 1.9764 | 3.0161 | 3.9965 | 5.0597
| Electricity consumption for buses |  |  |  |  | 0.051446 | 0.076229 | 0.10101 | 0.1258 | 0.15058 | 0.17536 | 0.20015
| Electricity consumption for trucks |  |  |  |  | 0.0021066 | 0.0035531 | 0.0059017 | 0.0097212 | 0.016069 | 0.026474 | 0.052173
| Electricity consumption for rail transport (incl. Metro and trams) |  | Computed | N/A | Macro-eco - Growth rate of gross personal disposable income | 1.45 | 1.4 | 1.36 | 1.31 | 1.27 | 1.22 | 1.18
Buildings and appliances | Appliances own: computer | Number per households | Computed | N/A | Macro-eco - Growth rate of gross personal disposable income | 1.37 | 1.39 | 1.41 | 1.43 | 1.45 | 1.47 | 1.5
| Appliances own: dishwasher |  |  |  |  | 0.45 | 0.46 | 0.46 | 0.47 | 0.47 | 0.48 | 0.48
| Appliances own: dryer |  |  |  |  | 0.77 | 0.78 | 0.79 | 0.8 | 0.8 | 0.81 | 0.82
| Appliances own: freezer |  |  |  |  | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.88
| Appliances own: fridge |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Appliances own: others |  |  |  |  | 0.8 | 0.8 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
| Appliances own: tv |  |  |  |  | 2.46 | 2.49 | 2.53 | 2.57 | 2.6 | 2.64 | 2.67
| Appliances own: wmachine |  |  |  |  | 0.97 | 0.97 | 0.98 | 0.98 | 0.99 | 0.99 | 1
| Appliances use: computer | hour/year |  |  |  | 887 | 890 | 893 | 896 | 899 | 902 | 905
| Appliances use: dishwasher |  |  |  |  | 642 | 643 | 644 | 645 | 647 | 648 | 649
| Appliances use: dryer |  |  |  |  | 278 | 279 | 280 | 281 | 283 | 284 | 285
| Appliances use: freezer |  |  |  |  | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
| Appliances use: fridge |  |  |  |  | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
| Appliances use: others |  |  |  |  | 37 | 37 | 37 | 37 | 38 | 38 | 38
| Appliances use: tv |  |  |  |  | 2026 | 2034 | 2041 | 2049 | 2056 | 2064 | 2071
| Appliances use: wmachine |  |  |  |  | 891 | 894 | 897 | 900 | 903 | 906 | 909
| Living space per person | m²/cap |  |  |  | 56 | 56 | 56 | 56 | 56 | 56 | 56
| Renovation rate for all buildings | %/year | Computed | N/A | Pathways Explorer lever - 'Buildings renovation rate' set on level 1 See accompanying document for justification | 0.74% | 0.77% | 0.81% | 0.84% | 0.88% | 0.91% | 0.95%
| Electricity consumption for heating - direct electricity heating + circulation pumps for all heating systems | TWh/year | Computed. Includes electricity consumption from circulation pumps for all heating systems, irrespective of the fuel used | N/A | Pathways Explorer lever - 'Electrification of space and water heating' set on level 2 See accompanying document for justification | 9.21 | 9.26 | 9.32 | 9.38 | 9.44 | 9.5 | 9.56
| Electricity consumption for heating - heat pumps |  | External | Elia trajectories for the AdeqFlex 23 study | N/A | 0.97 | 1.1 | 1.27 | 1.48 | 1.72 | 1.97 | 2.23
Industry production | Industry sector production level: aluminium | kt/year | Computed | N/A | Macro-eco - Growth rate of industry added value for the intermediate goods. Kept constant here because the economic growth came from pharmaceuticals which have only a marginal impact on electrcity consumption. | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Industry sector production level: cement |  |  |  |  | 4647 | 4647 | 4647 | 4647 | 4647 | 4647 | 4647
| Industry sector production level: ceramic |  |  |  |  | 2608 | 2608 | 2608 | 2608 | 2608 | 2608 | 2608
| Industry sector production level: chemical-ammonia |  |  |  |  | 979 | 979 | 979 | 979 | 979 | 979 | 979
| Industry sector production level: chemical-chlorine |  |  |  |  | 763 | 763 | 763 | 763 | 763 | 763 | 763
| Industry sector production level: chemical-olefin |  |  |  |  | 1960 | 1960 | 1960 | 1960 | 1960 | 1960 | 1960
| Industry sector production level: chemical-other |  |  |  |  | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551
| Industry sector production level: food |  |  |  |  | 7826 | 7826 | 7826 | 7826 | 7826 | 7826 | 7826
| Industry sector production level: glass |  |  |  |  | 1608 | 1608 | 1608 | 1608 | 1608 | 1608 | 1608
| Industry sector production level: lime |  |  |  |  | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015
| Industry sector production level: non-ferrous |  |  |  |  | 1402 | 1402 | 1402 | 1402 | 1402 | 1402 | 1402
| Industry sector production level: steel |  |  |  |  | 7982 | 7982 | 7982 | 7982 | 7982 | 7982 | 7982
| Industry sector production level: other-industries |  |  | N/A | Macro-eco - Growth rate of industry added value for capital and consumption goods | 5689 | 5746 | 5810 | 5847 | 5882 | 5935 | 5986
| Industry sector production level: paper |  |  |  |  | 2470 | 2484 | 2507 | 2519 | 2534 | 2552 | 2569
| Industry sector production level: wood |  |  |  |  | 492 | 495 | 499 | 502 | 505 | 508 | 512

## 2.3 Demand-Side Response
2.2 Demand-Side Response
a) Definition in the ERAA methodology regarding Demand-Side Response (DSR):
'explicit demand-side response’ (explicit DSR) means the change of electric demand pursuant to an accepted offer to sell demand reduction or increase in an organised market, either directly or through aggregation. Explicit DSR may consist of either foregone or time-shifted demand;
‘implicit demand-side response’ (implicit DSR) means the change of demand by final customers from their normal or current consumption patterns, in response to time-variable electricity prices or incentive payments. Implicit DSR can either be self-directed or directed by an energy management service provider;
The figures below include the explicit and implicit Demand-Side Response
Demand-side response volume
DSR - Capacity in reference scenario | Total capacity [MW]
| 2025-2026 | 2028-2029
Max use of 1 hour | 130 | 130
Max use of 2 hours | 453 | 453
Max use of 4 hours* | 634 | 634
Max use of 8 hours | 388 | 388
No limit | 193 | 193
Total | 1798 | 1798
* The volume for ancillary services is included in the "max use of 4 hours" category
Potentially DSR added during calibration (shedding capacity) | Total capacity [MW]
| 2025-2026 | 2028-2029
Total | 450 | 900
Additional DSR from industry electrification (shedding capacity) | % of the additional electrification by industry
| 2025-2026 | 2028-2029
P2H - HP | 80
P2H - eBoiler | 100
DRI-EAF (Steel) | 75
CCS | 0
Data centers | 50
Sources:
Public consultation of Adequacy & Flexibility study 2023

## 3. Balancing capacity
3. Balancing capacity
Volume [MW]
| 2025-2026 | 2028-2029
Total FCR | 95 | 97
Total FRR | 1221 | 1353
Total reserve capacity | 1316 | 1450

## 4. Flow based domains
4. Flow based domains
Elia has developed a flow-based framework which does not rely on historical domains, but instead aims to mimic the operational flow-based capacity calculation workflow.
The framework is based on a zonal model of Europe, the grid model used is based on the TYNDP 2022.
The flow-based perimeter includes the CORE region, with 13-dimensional domains.
Using a framework allows hence to consult on the parameters rather than domains.
The flow-based domains will be illustrated in the final report.
For more information on flow-based please refer to the public consultation on methodology:
4.1.1. Main parameters
Market Parameters | 2025 | 2028
Flow-based perimeter | CORE | CORE
Bidding zones | AS IS | AS IS
minRAM | See table below | See table below
Treatment of external flows | Advanced Hybrid Coupling (AHC) | Advanced Hybrid Coupling (AHC)
External constraints | No external constraints | No external constraints
Use of PST in capacity calculation | For Belgium: 1/2 For other: 1/3 | For Belgium: 1/2 For other: 1/3
Use of HVDC in flow-based capacity allocation | Only ALEGrO | Only ALEGrO
4.1.2. MinRAM trajectories
Country | 2025 | 2028
Netherlands | 70 | 70
Belgium
Germany
France
Slovenia
Hungary
Kroatia
Romania
Czechia
Austria
Slovakia
Poland

## 5. Other countries data
5. Sources for other countries
Sources :
European Resource Adequacy Assessment 2022 from ENTSO-E |  |  | https://www.entsoe.eu/outlooks/eraa/
The sources for the proposed updates are presented in the explanatory note.
Updates proposed :
2025-2026 | France | Germany | Netherlands | United Kingdom | Spain | Italy | Poland | Denmark
Demand [TWh] | 480 | 574 | 124 | 295 | 259 | 329 | 167 | 41
Onshore Wind [GW] | 25 | 77 | 10 | 20 | 37 | 14 | 11 | 6
Offshore Wind [GW] | 2 | 11 | 6 | 23 | 0 | 3 | 0.6 | 3
Solar [GW] | 24 | 108 | 34 | 21 | 34 | 43 | 20 | 8
Coal [GW] | 1.1 | 25.1 | 2.7 | 0 | 0 | 0.5 | 20.7 | 0.4
Nuclear [GW] | 62.9 | 0 | 0.5 | 5.9 | 7.1 | 0 | 0 | 0
2028-2029 | France | Germany | Netherlands | United Kingdom | Spain | Italy | Poland | Denmark
Demand [TWh] | 506 | 619 | 141 | 316 | 261 | 342 | 178 | 50
Onshore Wind [GW] | 27 | 99 | 11 | 27 | 45 | 17 | 11 | 7
Offshore Wind [GW] | 3 | 15 | 12 | 36 | 0 | 6 | 6 | 5
Solar [GW] | 40 | 172 | 43 | 29 | 50 | 62 | 25 | 15
Coal [GW] | 0 | 7.4 | 2.7 | 0 | 0 | 0 | 20.3 | 0.4
Nuclear [GW] | 62.9 | 0 | 0.5 | 4.4 | 5.1 | 0 | 0 | 0

## 6. Economic parameters
6. Economic parameters
The prices are based on "Announced Pledges" scenario from WEO2021 and are expressed in € 2022.
Category | Price [€ 2022/MWh]
| 2025-2026 | 2028-2029
Oil | 35.5 | 28
Gas | 18.6 | 11.4
Coal | 36.7 | 34.9
Price [€ 2022/tCO2]
| 2025-2026 | 2028-2029
CO2 | 107 | 120.3

## 7. Proposed sensitivities
7. Proposed sensitivities
Sensitivity | Description | Applicable for Delivery year 2025-2026 | Applicable for Delivery year 2028-2029
French nuclear availability 1 | Y-1 DY2025-26 : Lower availability during winter compared to REMIT Calculated as the difference with the high EDF forecast on the winter only Y-4 DY2028-29 : Lower availability by 2 units on average during winter compared to ERAA | Yes | Yes
French nuclear availability 2 | Y-1 DY2025-26 : Lower availability during winter compared to REMIT Calculated as the difference with the high EDF forecast on the winter only Y-4 DY2028-29 : Lower availability by 4 units on average during winter compared to ERAA | Yes | Yes
French nuclear availability 3 | Y-1 DY2025-26 : Lower availability during winter compared to REMIT Calculated as the difference with the minimum EDF forecast on the winter only Y-4 DY2028-29 : Lower availability by 6 units on average during winter compared to ERAA | Yes | Yes
French nuclear availability 4 | Y-1 DY2025-26 : Lower availability during winter compared to REMIT Calculated as the difference with the minimum EDF forecast on the winter only Y-4 DY2028-29 : Lower availability by 8 units on average during winter compared to ERAA | Yes | Yes
UK nuclear availability | The nuclear units for which an extension was announced in the UK are not available | Yes | No
FB CEP rules | Non achievements of the CEP rules to reflect the uncertainty on capacity calculation. Fixed RAM 70% instead of 70% minRAM | Yes | Yes
Export restrictions in Norway | Norway blocking export of electricity due to low hydro production Export restrictions in Norway during periods of low hydro production | Yes | Yes
High prices in Europe | Higher prices in Europe Higher fuel costs | Yes | Yes
Low prices in Europe | Lower prices in Europe Lower fuel costs | Yes | Yes
Lower Demand in Belgium | Lower demand in Belgium Lower yearly consumption due to economic developments | Yes | Yes
Higher demand in Belgium due to high prices | Higher demand in Belgium due to high prices Higher yearly consumption due to economic developments | Yes | Yes
Higher existing DSR capacity in Belgium | Higher existing DSR capacity in Belgium Additional 50 % of potential DSR capacity considered as existing before calibration | Yes | Yes
Higher existing large-scale battery capacity in Belgium | Higher existing large-scale battery capacity in Belgium Additional 50 % of potential large-scale battery capacity considered as existing before calibration | Yes | Yes
TJ closure | Closure of turbojets due to possible CO2 threshold -140 MW | No | Yes

## 8. Preselected capacity types
8. Preselected capacity types
The preselected capacity types have the characteristics described in the tabel below.
For DY 2025-26
Category | Associated technology | Volume Calculation | Marginal Price Calculation | CAPEX | FOM | Economic lifetime
|  |  |  | [€ 2022/kW] | [€ 2022/kW] | [y]
Batteries | Large-scale bat. | Add new Large-scale batteries | / | 1200 | 20 | 15
DSR | DSR | Add new 4h DSR | Marginal price of 4h DSR | 0 | See below | 1
For DY 2028-29
Category | Associated technology | Volume Calculation | Marginal Price Calculation | CAPEX | FOM | Economic lifetime
|  |  |  | [€ 2022/kW] | [€ 2022/kW] | [y]
Type 1 - Semi-baseload | CCGT, CHP | Add new CCGT | Marginal price of a new CCGT | 700* | 30 | 20
Type 2 - Peakers 1 | OCGT | Add new OCGT | Marginal price of a new OCGT | 550** | 25 | 20
Type 4 - Batteries | Large-scale bat. | Add new Large-scale batteries | / | 900 | 20 | 15
Type 5 - DSR | DSR | Add new 4h DSR | Marginal price of 4h DSR | see below
*CAPEX for CCGT >800 MW: assumption under review in discussions with industry
**CAPEX for OCGT>100 MW

## 9. Scenarios post DY
9. Scenarios post-delivery period choice
Sources of scenarios for periods after the delivery period in order to calculate the market revenues.
Application to Y-1 auction for DY 2025-2026
Application to Y-4 auction for DY 2028-2029
2025
2028
2040
2026-27
AdFlex 23
AdFlex 23 (2034 Scenario)
2030
2032
2034
AdFlex 23
CRM Y-4
DY28-29
2028
2040
AdFlex 23
AdFlex 23 (2034 Scenario)
2030
2032
2034

## 10.1 IPC - Technology List
10.1 Intermediate Price Cap - Technology List
relevant for the Y-4 Auction for Delivery Period 2028-2029 and Y-1 Auction for Delivery Period 2025-2026
Technology (existing units) | Energy activation duration | Yearly Fixed O&M |  |  | Source
| hours | [€/kW/year]
|  | low | mid | high
CCGT | / | 37 | 38 | 53 | AFRY 2022
OCGT | / | 25 | 25 | 50 | AFRY 2022
Turbojet | / | 29 | 36 | 36 | AFRY 2022
Pump Storage | 4 | 20 | 32 | 40 | AFRY 2022
Market response | 4 | 7 | 12 | 17 | AdFlex 2023
WACC | 5.53%
Hurdle Premium | Annex 1, https://www.ejustice.just.fgov.be/eli/arrete/2021/04/28/2021041351/justel#LNK0008

## 10.2 IPC - Revenues parameters
10.2 Intermediate Price Cap - Input parameters for revenues
Input parameters for market revenues
Technologies | Efficiency [%] |  |  | VOM [€ 2022/MWh]
| low | mid | high | low | mid | high
CCGT | 50 | 54 | 58 | 2,4 | 2,4 | 2,4
OCGT | 35 | 40 | 44 | 13,2 | 13,2 | 13,2
Turbojet | 21 | 28 | 35 | 4 | 4 | 4
Activation cost of availability test
Activation cost, in €/kW-derated/year: |  | 0,82€/kWh*0,25h*(1/X) with X the derating factor (in %) associated to the SLA with a 4 hour energy activation constraint
Source: |  | https://www.elia.be/en/suppliers/supplier/energy-purchases/strategic-reserve-volume-and-prices