Data collection questionnaire

Table of contents

1.	Introduction	4

2.	Operational characteristics of the unit	5

3.	Generator information	7

4.	Alternator external parameter	7

5.	Step-up transformer	9

6.	Exciter and automatic voltage regulator (AVR)	10

6.1.	Over-excitation limiter	11

6.2.	Under-excitation limiter	11

6.3.	Power system stabiliser (PSS)	11

6.4.	In case of brushless exciter	11

6.5.	In case of static exciter	12

7.	Turbine-governor / prime mover	12

7.1.	General Data	12

7.2.	Gas turbine	13

7.3.	Steam turbine	13

7.4.	Combined-cycle	14

8.	Wind farm	14

8.1.	Wind turbine modelling parameters	14

8.1.1.	Induction generator parameters (Fixed-speed, variable-slip, DFIG)	14

8.1.2.	Permanent magnet alternator (Full converter)	15

8.1.3.	Converter parameters (DFIG, full converter)	15

8.1.4.	Pitch  and storm mitigation control (if relevant)	15

8.1.5.	Aerodynamic	15

8.2.	Wind turbine operational characteristics	16

8.3.	Wind park	16

8.3.1.	Possible compensation means and automatic voltage regulation of the park	17

9.	Auxiliaries	17

10.	Protections	18

11.	Appendix	19

11.1.	Appendix 1	19

11.2.	Appendix 2	21

# Introduction

In the frame of the electrical studies of the Belgian network, the objective of this document is to collect the required data in order to build the model of the production unit allowing static or dynamic simulations. This questionnaire does not replace the other demands of information that the TSO could require within the framework of his activities and in accordance with the grid code.

# Operational characteristics of the unit

- Connection node and voltage :                                       (             kV )

- Unit Type : please choose one type of unit in the table below

| CL : Classical | D : Diesel | GE : Gas Engine | GT : Gas Turbine |
| --- | --- | --- | --- |
| IS : Incineration Station | NU : Nuclear | ST : Steam Turbine | TJ : Turbo Jet |
| WKK : Cogeneration Unit | WT : Wind Turbine | BG : Biogas | PS : Pomp Station |
| HU : Hydraulic Unit | CCGT : Combined Cycle | CCGT-ST : Combined Cycle Steam Turbine | CCGT-GT : Combined Cycle Gas Turbine |

- Specific average consumption (GJ/MWh) :

Start fuel : please indicate below the fuel type used for machine start

- Start fuel 1 :

- Start fuel 2 (if applicable) :

- Start fuel 3 (if applicable) :

For every type of fuel of the unit, please select the fuel and fill in the related characteristics :

Fuel type 1 :

- Fuel type :

| BF : Blast Furnace Gas | CP : Coal pulverized | FA : Fuel A | GO : Gas Oil |
| --- | --- | --- | --- |
| LV : LVN | NG : Natural Gas | NU : Nuclear | WA : Water |
| WI : Wind | WR : Waste Recycle | CP/CG : Mix Coal - Cokes Gas | FA/BF : Mix Fuel A - Blast Furnace |
| CP/BF : Mix Coal - Blast Furnace | CG : Cokes Gas | CP/ST/BG: mix coal-steam-biogas |  |

- Ramping rate (MW/min) :

- Emergency Ramping Rate (MW/min) :

- Technical Pmin (MW) :

- Technical Pmax (MW) :

Fuel type 2 (if applicable) :

- Fuel type :

| BF : Blast Furnace Gas | CP : Coal pulverized | FA : Fuel A | GO : Gas Oil |
| --- | --- | --- | --- |
| LV : LVN | NG : Natural Gas | NU : Nuclear | WA : Water |
| WI : Wind | WR : Waste Recycle | CP/CG : Mix Coal - Cokes Gas | FA/BF : Mix Fuel A - Blast Furnace |
| CP/BF : Mix Coal - Blast Furnace | CG : Cokes Gas | CP/ST/BG: mix coal-steam-biogas |  |

- Ramping rate (MW/min) :

- Emergency Ramping Rate (MW/min) :

- Technical Pmin (MW) :

- Technical Pmax (MW) :

Fuel type 3 (if applicable) :

- Fuel type :

| BF : Blast Furnace Gas | CP : Coal pulverized | FA : Fuel A | GO : Gas Oil |
| --- | --- | --- | --- |
| LV : LVN | NG : Natural Gas | NU : Nuclear | WA : Water |
| WI : Wind | WR : Waste Recycle | CP/CG : Mix Coal - Cokes Gas | FA/BF : Mix Fuel A - Blast Furnace |
| CP/BF : Mix Coal - Blast Furnace | CG : Cokes Gas | CP/ST/BG: mix coal-steam-biogas |  |

- Ramping rate (MW/min) :

- Emergency Ramping Rate (MW/min) :

- Technical Pmin (MW) :

- Technical Pmax (MW) :

# Generator information

Manufacturer :

Type :

Year manufactured :

Snom	Rated apparent power (+ related ambient temperature)	MVA

Pnom	Rated active power (+ related ambient temperature)	MW

Unom	Rated terminal voltage	kV

ΔU+	Tolerance on the terminal voltage above the rated voltage	%

ΔU-	Tolerance on the terminal voltage under the rated voltage	%

Inom	Rated stator current at standard cooling condition	kA

Cos 	Rated power factor

nom	Rated speed	rpm

PD2alt	Moment of inertia (generator + excitator)	ton x m2

- Generator capability curves (An example is given in appendix 1).

- Please attach the saturation curves (An example is given in appendix 1).

- Diagram or tabular showing the evolution of the maximal  active and apparent power (Pmax and Smax) versus the cooling system (water temperature, ambient temperature and/or hydrogen pressure)

# Alternator external parameter

Remark : generally the manufacturer provides the alternator parameters in per unit base Snom (apparent rated power in MVA). It is important to specify the value of Snom. If the data are also provided in Ohm, please indicate them.

SN	Reference value used for per unit calculation 	MVA

Ra	Stator resistance	pu

Ta	Stator time constant	s

Xl	Stator leakage reactance	pu

Xd	Direct-axis unsaturated reactance	pu

X'd	Direct-axis unsaturated transient reactance	pu

X"d	Direct-axis unsaturated sub-transient reactance	pu

Xq	Quadrature-axis unsaturated reactance	pu

X'q	      Quadrature-axis unsaturated transient reactance			          pu

X"q	Quadrature-axis unsaturated sub-transient reactance	pu

T'd0	Direct-axis transient open circuit time constant	s

T"d0	Direct-axis sub-transient open circuit time constant	s

T'q0	Quadrature-axis transient open circuit time constant	s

T"q0	Quadrature-axis sub-transient open circuit time constant	s

H	 Inertia (all rotating mass)	s

X0	Unsaturated zero sequence reactance	pu

X2	Unsaturated negative sequence reactance	pu

R0	Zero sequence resistance	pu

R2	Negative sequence resistance	pu

# Step-up transformer

Snom	Apparent nominal power	MVA

Unom1	Machine-side nominal voltage	kV

Unom2	Network-side nominal voltage	kV

Xcc	Short circuit reactance	Ucc%

PCu	Copper losses	kW

PFe	Iron losses	kW

Im	Magnetising current	A

- Connection and earthing of the transformer windings (ex Yd11)

- Possible ground connection impedance (at primary and/or secondary winding)?

- Connection of an auxiliary tertiary winding in delta?

- Shell or Core type transformer?

- Free or forced fluxes magnetic path?

- Xcc13 et Xcc23 : Short circuit reactance primary-tertiary and secondary-tertiary

- PCu13 et PCu23 : Copper losses primary-tertiary and secondary-tertiary

- If the magnetic path is forced (three-legged core type transformer):

Xcc0	Zero sequence short circuit reactance	Ucc%

PCu0	Zero sequence copper losses	kW

PFe0	Zero sequence iron losses	kW

Im0	Zero sequence magnetising current	A

- Moreover, in case of tertiary winding :

Xcc013 et Xcc023 : Zero sequence short circuit reactance primary-tertiary and secondary-tertiary

PCu013 et PCu023 : Zero sequence copper losses primary-tertiary and secondary-tertiary

- Is the transformer equipped with a tap changer? If yes, please provide the following data:

- Regulated side (machine or network)

- Number of taps and voltage variation per tap (in kV or in %)

- Under load tap changer?

- Present tap setting

- Is it equipped with an automatic tap controller (for example, automatic tap modification to keep a constant voltage) ? If yes :

- regulating voltage range

- dead band

- delay in second between 2 tap changes

- Magnetic saturation curve

- For the wind farm, please indicate the data regarding the step-up transformer to the network and the data regarding the LV-MV transformer associated to each turbine (indicate if there is different types)

# Exciter and automatic voltage regulator (AVR)

Excitation system used (static exciter, rotating AC alternator exciter,…):

Manufacturer :

Type :

Ir_nom	Rated exciter current	A

Ur_nom	Rated exciter output voltage	V

Ur_max	Maximum permanent exciter output voltage	V

Ur_min	Minimum permanent exciter output voltage	V

Ir_ceil	Maximum exciter current (ceiling value)	A

Ur_ceil	Maximum exciter output voltage (ceiling value)	V

Regulating range (automatic loop)	%Un

Reactive current voltage sensitivity range (droop)	± % d(U/Unom)/d(Iq/Inom)

Actual reactive current voltage sensitivity  	%

- For U = Unom and P = Pnom, what is the maximum reactive power, the ceiling value (QMAXPNOM) that enables the over-excitation limiter that brings back the reactive production to a fold-back value and this fold-back value (QMAXlim)?

- Is the regulator equipped with an adjustment loop of reactive production and/or power factor? What is the time constant of this loop?

- Does the voltage regulation use a stator current limitation? If yes :

- Activation threshold

- Activation delay in second

- Block diagram of the excitation system with the feedback loops and the associated limiters, with the value of the different parameters (an example of such a diagram block is given in appendix 2).

- Available tests reports of the voltage regulator.

## Over-excitation limiter

- Is the machine equipped with an over-excitation limiter?

- What is the activation threshold (% rated exciter output voltage)?

- What is the activation delay? (if the delay depends on the over shoot, please attach a plot of the evolution or the pair value (%Ur_nom, temporisation) )

- What is the over-excitation reset criterion?

- Please depict on the capability curves of the alternator, the limiter characteristic in the P (active production) – Q (reactive production) plane.

## Under-excitation limiter

- Is the machine equipped with an under-excitation limiter?

- What is the activation threshold (% rated exciter output voltage)?

- What is the activation delay?

- What is the under-excitation reset criteria?

- Please depict on the capability curves of the alternator, the limiter characteristic in the P (active production) – Q (reactive production) plane.

## Power system stabiliser (PSS)

- Is the unit equipped with a PSS? if Yes

- Is it activated ?

- What is (are) the input(s) of the PSS?

- Block diagram of the regulating loop of the PSS and the values of the time constants and the gain (An example is given in appendix 2).

- Available tests report of the PSS and the possible modification of the parameters.

## In case of brushless exciter

- Stator voltage output of the main alternator

- Excitation current of the main alternator

- Excitation voltage of the main alternator

- Output voltage (before rectification by the bridge) of the brushless

- Excitation current of the brushless

- Excitation voltage of the brushless

For the following operating points of the main alternator :

- at no load

- at nominal power

Every limitation must be mentioned (either due to the thyristors controlling the brushless or due to the diode bridge of the brushless, or others).

Tables or graphical representations linking the above required data by pairs are accepted.

## In case of static exciter

Data regarding the exciter transformer:

Snom	Rated apparent power	MVA

U1	alternator-side rated voltage	kV

U2	Network-side rated voltage	kV

Xcc	Short-circuit reactance	Ucc%

- Other comments regarding the automatic voltage regulation:

…

# Turbine-governor / prime mover

## General Data

Manufacturer :

Type :

Energy source :

Pmax	Maximum active power output	MW

Pmin	Minimum active power output	MW

Pnom	Rated active power (related ambient temperature)	MW

PD²turb	Turbine moment of inertia	ton x m²

PD²tot	Global unit moment of inertia (alternator + turbine + gear box)	ton x m²

- If available, the torsionnal analysis of the global shaft

- If the unit is equipped with a speed governor control:

Droop setting:

Dead band:

Power range for the speed control:

- Block diagram (transfer functions and non-linearities) of the turbine (or prime mover), the valves (or gates), the speed governor system, the different feedback loops and the limiters, with the related numerical data.

- Any time constants you have from the manufacturer describing the speed response of the governor. Be sure to identify each time constant (combustion, steam drum,…).

For gas turbines, steam turbines, combined cycles and wind farms, specific informations are required. Please provide them by filling the appropriate section hereunder

## Gas turbine

- Description of the different regulators et limiters :

- Temperature limiters at the turbine access

- IGV control and influence on the air flow

- Fuel flow regulation

- Limitation of the flame temperature, compressor surging, acceleration limiter, etc.…

- Documents showing the performance characteristics of the gas turbine. For different ambient temperatures and for different load factors:

- the electrical power at the alternator output terminal

- the fuel flow

- the turbine output temperature

- the exhaust flow

## Steam turbine

- Block diagram of the steam turbine with the control laws and the limiters.

- Interaction type between the turbine and the boiler (turbine follow mode, boiler follow mode,…)

- Block diagram of the boiler and its parameters (pressure control, temperature limiter, time constants,…) or if these data are not available, technical information necessary for their calculation (volume, limiters,…).

- Does the turbine system have a reheat process (i.e., both high- and low-pressure turbine) ?

- For a steam turbine, indicate the percent of full load power produced by each turbine :

LP turbine :			%

MP turbine:			%

HP turbine:			%

- Does the steam turbine have a fast valving system? If yes :

- activation criteria

- valves closing speed

- Other comments regarding the speed regulator/ prime mover governor :

…

## Combined-cycle

- Fill in the part 7.2 and 7.3 concerning the gas turbine, the steam turbine, and the waste heat boiler

- Indicate the percent of full load power produced by each component:

Gas turbine  :		%

Steam turbine  :		%

# Wind farm

## Wind turbine modelling parameters

Basic wind turbine generator parameters should be provided as following:

- Manufacturer, model and type ( precise the number of each type if different manufacturers or models)

- Rated power of each type of turbine

- Power calculation from wind speed

- Hub high

- Number of blades

- Rotor diameter

- Cut-in, Cut-out and rated wind speed

### Induction generator parameters (Fixed-speed, variable-slip, DFIG)

Rs	stator resistance 	Ω

Rr	rotor resistance	Ω

Xs	stator reactance	Ω

Xr	rotor reactance	Ω

Xm	rotor-stator mutual reactance	Ω

H	inertia	s

### Permanent magnet alternator (Full converter)

Refer to §3 and §4.

### Converter parameters (DFIG, full converter)

- Buck and boost, rectifier model

- Inverter model

- Filters

### Pitch  and storm mitigation control (if relevant)

- Block diagram of the stall/pitch control with the parameter values

- Storm mitigation pitch control blocs and parameters

Betamin	minimum pitch angle	deg

Betamax	maximum pitch angle	deg

Vcbeta	maximal speed variation of the pitch (increasing)	deg/s

Vdbeta	maximal speed variation of the pitch (decreasing)	deg/s

### Aerodynamic

Aerodynamic and mechanical drivetrain models along with characteristic curves of the electrical power versus the wind speed, the rotor speed versus the wind speed and the pitch angle versus the wind speed.

Nmin	minimum rotor speed 	rpm

Nmax	maximum rotor speed	rpm

Vmin	wind cut in speed	m/s

Vmax	wind cut off speed	m/s

Vrtd	wind speed when P = Pmax and pitch angle = 0	m/s

Rpal	blades radius	m

Tbase	rated torque on the low-speed shaft side	N m

Mred	gearbox ratio

## Wind turbine operational characteristics

#### Control and network interactions

- Behaviour in case of short-circuit

- Behaviour in case of abrupt change of short circuit power at the point of common connection.

- Overall wind behaviour in case of sustained high speed profile

- Disconnection criteria + corresponding delay and disconnection time

- Reconnection criteria + corresponding delay and reconnection time

- Maximum power injected or absorbed from the network by the grid side converted

- Capability curves of a wind turbine (of each type) (P-Q curves).

If present, describe the compensation means associated with each turbine.

- Available tests reports (certified wind curve, power quality certificate, wind statistic,…)

- Is the wind turbine equipped with a Star/delta configuration switch?

If yes, criterion to switch from a configuration to the other

#### Ancillary services

- Fault ride through capability (curve)

- Low voltage support (Reactive current voltage sensitivity (droop))

- Active power control (Active power frequency sensitivity)

## Wind park

- Number of wind turbines  and their GPS position

- Power curve of each type of turbine (if different)

- Single-line diagram of the wind farm

  - Characteristics of the cables (type, length) and transformers

  - Compensation means and characteristics

  - The data related to the transformer associated to each wind turbine have to be given coherently with section 5

  - Filters (if existing) and characteristics

- Capability curves of the whole wind farm (P-Q curves) for at least the following voltages (0.9pu, 1 pu and 1.1pu) at the point of common coupling. The capability curves should include possible other limitations (e.g. temperature...)

- Characteristic curve of the power delivered by the wind park versus the wind speed

- Equivalent dynamical model for transient RMS simulation at the point of common coupling. The model should reflect at least the behaviours tested during the conformity study and represent the behaviour “as built”.

### Possible compensation means and automatic voltage regulation of the park

Capacitor bank (power, number of steps, settings of the voltage control)

Harmonic filter (resonant frequency, type)

Static compensator (power, type)

Description, logic and settings of the Automatic Voltage Control of the wind park

Other comments regarding the compensation means:

# Auxiliaries

Type :

Paux	Maximum active power consumed by the auxiliaries	MW/kW

Qaux	Maximum reactive power consumed by the auxiliaries	MVAr/kVAR

- Specific protections of the auxiliaries (especially voltage and frequency) :

- Type

- Available settings

- Present settings

- Please attach the curves showing the variation of the auxiliaries consumption versus the output power of the generator. If they are not available, provide the consumption for a zero-, minimum-, rated- and maximum generator output power.

- If the auxiliaries are fed through a transformer, please provide also the data requested for the step up transformer at point 4.

- Backup power in case of not-energized point of common coupling

- Other comments regarding the auxiliaries:

…

# Protections

Characteristics of the generator and park protections:

- Frequency relay (under and over frequency)

- Over- and under-voltage protection

- Stator thermal protection / over current protection

- Reverse power relay

- Loss of synchronism protection

- Volts/Hz protection

- Current unbalance (negative sequence) protection

- Stator winding ground fault protection

- Internal park protections philosophy (e.g. differential...)

- Other protections...

# Appendix

## Appendix 1

Saturation curves example:

Saturation curves example:

## Appendix 2

AVR and PSS block diagram example:

The model should have characteristics in line with the standard IEC 61400-27.